## Read Me
ASHRAE Standard 140-2023
Informative Annex B16, Section B16.7.2 Example Results
for
Section 11, Constant Volume and Variable Air Volume Systems
AE301 through AE445
This spreadsheet contains the Informative Annex B16, Section B16.7.2 example results.
Users interested in looking at the example result tables and figures should go to the "Table List"
and "Figure List" sheets for a listing of tables and figures and their locations.
This spreadsheet can also be used to compare new results with the example results.
To add new results go to sheet "Adding Results" (2nd tab), cell A6 for instructions.
Results are added to sheet "Your Data" (3rd tab) and will automatically appear in the tables and figures.
To print example results or example results with new user generated results go to sheet "Title Page"
(4th tab) and follow the instructions starting in cell B5.
SHEET GUIDE
"Read Me" : General directions to using this workbook.
"Adding Results" : Instructions for adding new results, and map to example result and "YourData" worksheets.
"YourData" : For tested program results if doing comparison
"Title Page" : Sets headers for tables and charts and provides cover sheet to example results or new comparison results; see instructions on page.
"Program List" : Documentation of simulation programs used to produce informative Annex B16, Section B16.7.2 example results
"Table List": List of Informative Annex B16, Section B16.7.2 Tables in workbook with locations.
"Figure List": List of Informative Annex B16, Section B16.7.2 Figures in workbook with locations.
"Tables 1" through "Delta Tables 2" : Formatted result tables
"Fig B16.7.2-1 TotalCoil H+C" through "Fig B16.7.2-35 VAV dEcono" : Figures
"Detailed Location Results": Tool to compare detailed results
"Aggregate Results Final" : Unformatted results for use in tables and charts.
"Delta Results Final": Unformatted delta results for use in tables and charts.
Individual Example Results Worksheets as follows:
QAS: QAS model results set, 12Nov2014. Submitted by National Renewable Energy Laboratory, Golden, Colorado, United States.
DEEAP: DEEAP model results set, 10Dec2012. Submitted by AAON, Inc., Tulsa, Oklahoma, United States.
DeST: DeST 2 model results set, 21Nov2013. Submitted by Tsinghua University, Beijing, China.
DOE22: DOE-2.2 model results set, 10Mar2015. Submitted by National Renewable Energy Laboratory, Golden, Colorado, United States.
EPlus: EnergyPlus 8.2 model results set, 15Jan2015. Submitted by GARD Analytics, Arlington Heights, Illinois, United States.
IES-VE: IES-VE model results set, 20Feb2015. Submitted by Integrated Environmental Solutions, Glasgow, United Kingdom.
TRNSYS: TRNSYS-17 with TESS libraries model results set, 18Nov2014. Submitted by TESS, Madison, Wisconsin, United States.

## Adding Results
Output spreadsheet for Airside HVAC Equipment Diagnostic Tests: AE101 through AE445
New result data can be imported into this workbook and will automatically be included in tables and charts.
INSTRUCTIONS FOR ADDING NEW RESULTS
Import data so that Cell C50 of Std140_AE_Output.xls is in C50 of Sheet "YourData"
Check that the summary results for Case AE101 start at YourData!C61.
Data should flow to "YourData" cells as tabulated below. Your data will then appear in the rightmost column
of each table on sheets "Tables 1" to "Delta Tables 2". Charts are also updated with "your data" automatically.
Complete the program information block on "YourData", which is used for legend titles for the tables and graphs.
CELL ADDRESS GUIDE FOR EXAMPLE RESULT SHEETS AND NEW RESULTS
Gives locations for data in "YourData" sheet and in participant sheets.
Program Information Block - complete blue boxes to identify program and organization for report
| Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
| I5 | [5 empty] | O5
| Program Version Release Date: |  |  |  | I6 |  | Modeler Organization for Tables and Charts (short): |  |  |  | O6
| Program Name for Tables and Charts (short): |  |  |  | I7
| Results Submission Date: |  |  |  | I8 |  | Model / Organization Indentifier for Charts (short): |  |  |  | O8 | defaults to short program name / short organization name
Results
| Software: | C50
| Version: | C51
| Date: | C52
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | C61 | D61 | E61 | F61 | G61 | H61 | I61 | J61 | [5 empty] | AE101 | Dry bulb temperature (°C) | S61 | T61 | U61 | V61 | W61 | X61 | Y61
| AE103 | C62 | D62 | E62 | F62 | G62 | H62 | I62 | J62 | [6 empty] | Humidity ratio (g/gda) | S62 | T62 | U62 | V62 | W62 | X62 | Y62
| AE104 | C63 | D63 | E63 | F63 | G63 | H63 | I63 | J63 | [6 empty] | Specific volume (L/kgda) | S63 | T63 | U63 | V63 | W63 | X63 | Y63
[16 empty] | Enthalpy (J/gda) | S64 | T64 | U64 | V64 | W64 | X64 | Y64
[16 empty] | Mass flow rate (kgda/s) | S65 | T65 | U65 | V65 | W65 | #N/A | Y65
[15 empty] | AE103 | Dry bulb temperature (°C) | S66 | T66 | U66 | V66 | W66 | X66 | Y66
[16 empty] | Humidity ratio (g/gda) | S67 | T67 | U67 | V67 | W67 | X67 | Y67
[16 empty] | Specific volume (L/kgda) | S68 | T68 | U68 | V68 | W68 | X68 | Y68
[16 empty] | Enthalpy (J/gda) | S69 | T69 | U69 | V69 | W69 | X69 | Y69
[16 empty] | Mass flow rate (kgda/s) | S70 | T70 | U70 | V70 | W70 | #N/A | Y70
[15 empty] | AE104 | Dry bulb temperature (°C) | S71 | T71 | U71 | V71 | W71 | X71 | Y71
[16 empty] | Humidity ratio (g/gda) | S72 | T72 | U72 | V72 | W72 | X72 | Y72
[16 empty] | Specific volume (L/kgda) | S73 | T73 | U73 | V73 | W73 | X73 | Y73
[16 empty] | Enthalpy (J/gda) | S74 | T74 | U74 | V74 | W74 | X74 | Y74
[16 empty] | Mass flow rate (kgda/s) | S75 | T75 | U75 | V75 | W75 | #N/A | Y75
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | C89 | D89 | E89 | F89 | G89 | H89 | I89 | J89 | [5 empty] | AE201 | Dry bulb temperature (°C) | S89 | T89 | U89 | V89 | W89 | X89 | Y89 | Z89
| AE203 | C90 | D90 | E90 | F90 | G90 | H90 | I90 | J90 | [6 empty] | Humidity ratio (g/gda) | S90 | T90 | U90 | V90 | W90 | X90 | Y90 | Z90
| AE204 | C91 | D91 | E91 | F91 | G91 | H91 | I91 | J91 | [6 empty] | Specific volume (L/kgda) | S91 | T91 | U91 | V91 | W91 | X91 | Y91 | Z91
| AE205 | C92 | D92 | E92 | F92 | G92 | H92 | I92 | J92 | [6 empty] | Enthalpy (J/gda) | S92 | T92 | U92 | V92 | W92 | X92 | Y92 | Z92
| AE206 | C93 | D93 | E93 | F93 | G93 | H93 | I93 | J93 | [6 empty] | Mass flow rate (kgda/s) | S93 | T93 | U93 | V93 | W93 | #N/A | Y93 | Z93
| AE226 | C94 | D94 | E94 | F94 | G94 | H94 | I94 | J94 | [5 empty] | AE203 | Dry bulb temperature (°C) | S94 | T94 | U94 | V94 | W94 | X94 | Y94 | Z94
| AE245 | C95 | D95 | E95 | F95 | G95 | H95 | I95 | J95 | [6 empty] | Humidity ratio (g/gda) | S95 | T95 | U95 | V95 | W95 | X95 | Y95 | Z95
[16 empty] | Specific volume (L/kgda) | S96 | T96 | U96 | V96 | W96 | X96 | Y96 | Z96
[16 empty] | Enthalpy (J/gda) | S97 | T97 | U97 | V97 | W97 | X97 | Y97 | Z97
[16 empty] | Mass flow rate (kgda/s) | S98 | T98 | U98 | V98 | W98 | #N/A | Y98 | Z98
[15 empty] | AE204 | Dry bulb temperature (°C) | S99 | T99 | U99 | V99 | W99 | X99 | Y99 | Z99
[16 empty] | Humidity ratio (g/gda) | S100 | T100 | U100 | V100 | W100 | X100 | Y100 | Z100
[16 empty] | Specific volume (L/kgda) | S101 | T101 | U101 | V101 | W101 | X101 | Y101 | Z101
[16 empty] | Enthalpy (J/gda) | S102 | T102 | U102 | V102 | W102 | X102 | Y102 | Z102
[16 empty] | Mass flow rate (kgda/s) | S103 | T103 | U103 | V103 | W103 | #N/A | Y103 | Z103
[15 empty] | AE205 | Dry bulb temperature (°C) | S104 | T104 | U104 | V104 | W104 | X104 | Y104 | Z104
[16 empty] | Humidity ratio (g/gda) | S105 | T105 | U105 | V105 | W105 | X105 | Y105 | Z105
[16 empty] | Specific volume (L/kgda) | S106 | T106 | U106 | V106 | W106 | X106 | Y106 | Z106
[16 empty] | Enthalpy (J/gda) | S107 | T107 | U107 | V107 | W107 | X107 | Y107 | Z107
[16 empty] | Mass flow rate (kgda/s) | S108 | T108 | U108 | V108 | W108 | #N/A | Y108 | Z108
[15 empty] | AE206 | Dry bulb temperature (°C) | S109 | T109 | U109 | V109 | W109 | X109 | Y109 | Z109
[16 empty] | Humidity ratio (g/gda) | S110 | T110 | U110 | V110 | W110 | X110 | Y110 | Z110
[16 empty] | Specific volume (L/kgda) | S111 | T111 | U111 | V111 | W111 | X111 | Y111 | Z111
[16 empty] | Enthalpy (J/gda) | S112 | T112 | U112 | V112 | W112 | X112 | Y112 | Z112
[16 empty] | Mass flow rate (kgda/s) | S113 | T113 | U113 | V113 | W113 | #N/A | Y113 | Z113
[15 empty] | AE226 | Dry bulb temperature (°C) | S114 | T114 | U114 | V114 | W114 | X114 | Y114 | Z114
[16 empty] | Humidity ratio (g/gda) | S115 | T115 | U115 | V115 | W115 | X115 | Y115 | Z115
[16 empty] | Specific volume (L/kgda) | S116 | T116 | U116 | V116 | W116 | X116 | Y116 | Z116
[16 empty] | Enthalpy (J/gda) | S117 | T117 | U117 | V117 | W117 | X117 | Y117 | Z117
[16 empty] | Mass flow rate (kgda/s) | S118 | T118 | U118 | V118 | W118 | #N/A | Y118 | Z118
[15 empty] | AE245 | Dry bulb temperature (°C) | S119 | T119 | U119 | V119 | W119 | X119 | Y119 | Z119
[16 empty] | Humidity ratio (g/gda) | S120 | T120 | U120 | V120 | W120 | X120 | Y120 | Z120
[16 empty] | Specific volume (L/kgda) | S121 | T121 | U121 | V121 | W121 | X121 | Y121 | Z121
[16 empty] | Enthalpy (J/gda) | S122 | T122 | U122 | V122 | W122 | X122 | Y122 | Z122
[16 empty] | Mass flow rate (kgda/s) | S123 | T123 | U123 | V123 | W123 | #N/A | Y123 | Z123
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | C137 | D137 | E137 | F137 | G137 | H137 | I137 | J137 | K137 | L137 | M137 | N137 | O137 | AE301 | Dry bulb temperature (°C) | S137 | T137 | U137 | V137 | W137 | X137 | Y137 | Z137 | AA137 | AB137 | AC137
| AE303 | C138 | D138 | E138 | F138 | G138 | H138 | I138 | J138 | K138 | L138 | M138 | N138 | O138 |  | Humidity ratio (g/gda) | S138 | T138 | U138 | V138 | W138 | X138 | Y138 | Z138 | AA138 | AB138 | AC138
| AE304 | C139 | D139 | E139 | F139 | G139 | H139 | I139 | J139 | K139 | L139 | M139 | N139 | O139 |  | Specific volume (L/kgda) | S139 | T139 | U139 | V139 | W139 | X139 | Y139 | Z139 | AA139 | AB139 | AC139
| AE305 | C140 | D140 | E140 | F140 | G140 | H140 | I140 | J140 | K140 | L140 | M140 | N140 | O140 |  | Enthalpy (J/gda) | S140 | T140 | U140 | V140 | W140 | X140 | Y140 | Z140 | AA140 | AB140 | AC140
| AE306 | C141 | D141 | E141 | F141 | G141 | H141 | I141 | J141 | K141 | L141 | M141 | N141 | O141 |  | Mass flow rate (kgda/s) | S141 | T141 | U141 | V141 | W141 | X141 | Y141 | #N/A | #N/A | AB141 | AC141
| AE326 | C142 | D142 | E142 | F142 | G142 | H142 | I142 | J142 | K142 | L142 | M142 | N142 | O142 | AE303 | Dry bulb temperature (°C) | S142 | T142 | U142 | V142 | W142 | X142 | Y142 | Z142 | AA142 | AB142 | AC142
| AE345 | C143 | D143 | E143 | F143 | G143 | H143 | I143 | J143 | K143 | L143 | M143 | N143 | O143 |  | Humidity ratio (g/gda) | S143 | T143 | U143 | V143 | W143 | X143 | Y143 | Z143 | AA143 | AB143 | AC143
[16 empty] | Specific volume (L/kgda) | S144 | T144 | U144 | V144 | W144 | X144 | Y144 | Z144 | AA144 | AB144 | AC144
[16 empty] | Enthalpy (J/gda) | S145 | T145 | U145 | V145 | W145 | X145 | Y145 | Z145 | AA145 | AB145 | AC145
[16 empty] | Mass flow rate (kgda/s) | S146 | T146 | U146 | V146 | W146 | X146 | Y146 | #N/A | #N/A | AB146 | AC146
[15 empty] | AE304 | Dry bulb temperature (°C) | S147 | T147 | U147 | V147 | W147 | X147 | Y147 | Z147 | AA147 | AB147 | AC147
[16 empty] | Humidity ratio (g/gda) | S148 | T148 | U148 | V148 | W148 | X148 | Y148 | Z148 | AA148 | AB148 | AC148
[16 empty] | Specific volume (L/kgda) | S149 | T149 | U149 | V149 | W149 | X149 | Y149 | Z149 | AA149 | AB149 | AC149
[16 empty] | Enthalpy (J/gda) | S150 | T150 | U150 | V150 | W150 | X150 | Y150 | Z150 | AA150 | AB150 | AC150
[16 empty] | Mass flow rate (kgda/s) | S151 | T151 | U151 | V151 | W151 | X151 | Y151 | #N/A | #N/A | AB151 | AC151
[15 empty] | AE305 | Dry bulb temperature (°C) | S152 | T152 | U152 | V152 | W152 | X152 | Y152 | Z152 | AA152 | AB152 | AC152
[16 empty] | Humidity ratio (g/gda) | S153 | T153 | U153 | V153 | W153 | X153 | Y153 | Z153 | AA153 | AB153 | AC153
[16 empty] | Specific volume (L/kgda) | S154 | T154 | U154 | V154 | W154 | X154 | Y154 | Z154 | AA154 | AB154 | AC154
[16 empty] | Enthalpy (J/gda) | S155 | T155 | U155 | V155 | W155 | X155 | Y155 | Z155 | AA155 | AB155 | AC155
[16 empty] | Mass flow rate (kgda/s) | S156 | T156 | U156 | V156 | W156 | X156 | Y156 | #N/A | #N/A | AB156 | AC156
[15 empty] | AE306 | Dry bulb temperature (°C) | S157 | T157 | U157 | V157 | W157 | X157 | Y157 | Z157 | AA157 | AB157 | AC157
[16 empty] | Humidity ratio (g/gda) | S158 | T158 | U158 | V158 | W158 | X158 | Y158 | Z158 | AA158 | AB158 | AC158
[16 empty] | Specific volume (L/kgda) | S159 | T159 | U159 | V159 | W159 | X159 | Y159 | Z159 | AA159 | AB159 | AC159
[16 empty] | Enthalpy (J/gda) | S160 | T160 | U160 | V160 | W160 | X160 | Y160 | Z160 | AA160 | AB160 | AC160
[16 empty] | Mass flow rate (kgda/s) | S161 | T161 | U161 | V161 | W161 | X161 | Y161 | #N/A | #N/A | AB161 | AC161
[15 empty] | AE326 | Dry bulb temperature (°C) | S162 | T162 | U162 | V162 | W162 | X162 | Y162 | Z162 | AA162 | AB162 | AC162
[16 empty] | Humidity ratio (g/gda) | S163 | T163 | U163 | V163 | W163 | X163 | Y163 | Z163 | AA163 | AB163 | AC163
[16 empty] | Specific volume (L/kgda) | S164 | T164 | U164 | V164 | W164 | X164 | Y164 | Z164 | AA164 | AB164 | AC164
[16 empty] | Enthalpy (J/gda) | S165 | T165 | U165 | V165 | W165 | X165 | Y165 | Z165 | AA165 | AB165 | AC165
[16 empty] | Mass flow rate (kgda/s) | S166 | T166 | U166 | V166 | W166 | X166 | Y166 | #N/A | #N/A | AB166 | AC166
[15 empty] | AE345 | Dry bulb temperature (°C) | S167 | T167 | U167 | V167 | W167 | X167 | Y167 | Z167 | AA167 | AB167 | AC167
[16 empty] | Humidity ratio (g/gda) | S168 | T168 | U168 | V168 | W168 | X168 | Y168 | Z168 | AA168 | AB168 | AC168
[16 empty] | Specific volume (L/kgda) | S169 | T169 | U169 | V169 | W169 | X169 | Y169 | Z169 | AA169 | AB169 | AC169
[16 empty] | Enthalpy (J/gda) | S170 | T170 | U170 | V170 | W170 | X170 | Y170 | Z170 | AA170 | AB170 | AC170
[16 empty] | Mass flow rate (kgda/s) | S171 | T171 | U171 | V171 | W171 | X171 | Y171 | #N/A | #N/A | AB171 | AC171
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | C164 | D164 | E164 | F164 | G164 | H164 | I164 | J164 | K164 | L164 | M164 | N164 | O164 | AE401 | Dry bulb temperature (°C) | S185 | T185 | U185 | V185 | W185 | X185 | Y185 | Z185 | AA185 | AB185 | AC185
| AE403 | C165 | D165 | E165 | F165 | G165 | H165 | I165 | J165 | K165 | L165 | M165 | N165 | O165 |  | Humidity ratio (g/gda) | S186 | T186 | U186 | V186 | W186 | X186 | Y186 | Z186 | AA186 | AB186 | AC186
| AE404 | C166 | D166 | E166 | F166 | G166 | H166 | I166 | J166 | K166 | L166 | M166 | N166 | O166 |  | Specific volume (L/kgda) | S187 | T187 | U187 | V187 | W187 | X187 | Y187 | Z187 | AA187 | AB187 | AC187
| AE405 | C167 | D167 | E167 | F167 | G167 | H167 | I167 | J167 | K167 | L167 | M167 | N167 | O167 |  | Enthalpy (J/gda) | S188 | T188 | U188 | V188 | W188 | X188 | Y188 | Z188 | AA188 | AB188 | AC188
| AE406 | C168 | D168 | E168 | F168 | G168 | H168 | I168 | J168 | K168 | L168 | M168 | N168 | O168 |  | Mass flow rate (kgda/s) | S189 | T189 | U189 | V189 | W189 | X189 | Y189 | #N/A | #N/A | AB189 | AC189
| AE426 | C169 | D169 | E169 | F169 | G169 | H169 | I169 | J169 | K169 | L169 | M169 | N169 | O169 | AE403 | Dry bulb temperature (°C) | S190 | T190 | U190 | V190 | W190 | X190 | Y190 | Z190 | AA190 | AB190 | AC190
| AE445 | C170 | D170 | E170 | F170 | G170 | H170 | I170 | J170 | K170 | L170 | M170 | N170 | O170 |  | Humidity ratio (g/gda) | S191 | T191 | U191 | V191 | W191 | X191 | Y191 | Z191 | AA191 | AB191 | AC191
[16 empty] | Specific volume (L/kgda) | S192 | T192 | U192 | V192 | W192 | X192 | Y192 | Z192 | AA192 | AB192 | AC192
[16 empty] | Enthalpy (J/gda) | S193 | T193 | U193 | V193 | W193 | X193 | Y193 | Z193 | AA193 | AB193 | AC193
[16 empty] | Mass flow rate (kgda/s) | S194 | T194 | U194 | V194 | W194 | X194 | Y194 | #N/A | #N/A | AB194 | AC194
[15 empty] | AE404 | Dry bulb temperature (°C) | S195 | T195 | U195 | V195 | W195 | X195 | Y195 | Z195 | AA195 | AB195 | AC195
[16 empty] | Humidity ratio (g/gda) | S196 | T196 | U196 | V196 | W196 | X196 | Y196 | Z196 | AA196 | AB196 | AC196
[16 empty] | Specific volume (L/kgda) | S197 | T197 | U197 | V197 | W197 | X197 | Y197 | Z197 | AA197 | AB197 | AC197
[16 empty] | Enthalpy (J/gda) | S198 | T198 | U198 | V198 | W198 | X198 | Y198 | Z198 | AA198 | AB198 | AC198
[16 empty] | Mass flow rate (kgda/s) | S199 | T199 | U199 | V199 | W199 | X199 | Y199 | #N/A | #N/A | AB199 | AC199
[15 empty] | AE405 | Dry bulb temperature (°C) | S200 | T200 | U200 | V200 | W200 | X200 | Y200 | Z200 | AA200 | AB200 | AC200
[16 empty] | Humidity ratio (g/gda) | S201 | T201 | U201 | V201 | W201 | X201 | Y201 | Z201 | AA201 | AB201 | AC201
[16 empty] | Specific volume (L/kgda) | S202 | T202 | U202 | V202 | W202 | X202 | Y202 | Z202 | AA202 | AB202 | AC202
[16 empty] | Enthalpy (J/gda) | S203 | T203 | U203 | V203 | W203 | X203 | Y203 | Z203 | AA203 | AB203 | AC203
[16 empty] | Mass flow rate (kgda/s) | S204 | T204 | U204 | V204 | W204 | X204 | Y204 | #N/A | #N/A | AB204 | AC204
[15 empty] | AE406 | Dry bulb temperature (°C) | S205 | T205 | U205 | V205 | W205 | X205 | Y205 | Z205 | AA205 | AB205 | AC205
[16 empty] | Humidity ratio (g/gda) | S206 | T206 | U206 | V206 | W206 | X206 | Y206 | Z206 | AA206 | AB206 | AC206
[16 empty] | Specific volume (L/kgda) | S207 | T207 | U207 | V207 | W207 | X207 | Y207 | Z207 | AA207 | AB207 | AC207
[16 empty] | Enthalpy (J/gda) | S208 | T208 | U208 | V208 | W208 | X208 | Y208 | Z208 | AA208 | AB208 | AC208
[16 empty] | Mass flow rate (kgda/s) | S209 | T209 | U209 | V209 | W209 | X209 | Y209 | #N/A | #N/A | AB209 | AC209
[15 empty] | AE426 | Dry bulb temperature (°C) | S210 | T210 | U210 | V210 | W210 | X210 | Y210 | Z210 | AA210 | AB210 | AC210
[16 empty] | Humidity ratio (g/gda) | S211 | T211 | U211 | V211 | W211 | X211 | Y211 | Z211 | AA211 | AB211 | AC211
[16 empty] | Specific volume (L/kgda) | S212 | T212 | U212 | V212 | W212 | X212 | Y212 | Z212 | AA212 | AB212 | AC212
[16 empty] | Enthalpy (J/gda) | S213 | T213 | U213 | V213 | W213 | X213 | Y213 | Z213 | AA213 | AB213 | AC213
[16 empty] | Mass flow rate (kgda/s) | S214 | T214 | U214 | V214 | W214 | X214 | Y214 | #N/A | #N/A | AB214 | AC214
[15 empty] | AE445 | Dry bulb temperature (°C) | S215 | T215 | U215 | V215 | W215 | X215 | Y215 | Z215 | AA215 | AB215 | AC215
[16 empty] | Humidity ratio (g/gda) | S216 | T216 | U216 | V216 | W216 | X216 | Y216 | Z216 | AA216 | AB216 | AC216
[16 empty] | Specific volume (L/kgda) | S217 | T217 | U217 | V217 | W217 | X217 | Y217 | Z217 | AA217 | AB217 | AC217
[16 empty] | Enthalpy (J/gda) | S218 | T218 | U218 | V218 | W218 | X218 | Y218 | Z218 | AA218 | AB218 | AC218
[16 empty] | Mass flow rate (kgda/s) | S219 | T219 | U219 | V219 | W219 | X219 | Y219 | #N/A | #N/A | AB219 | AC219

## YourData
Output spreadsheet for Airside Mechanical Equipment Diagnostic Tests: AE101 through AE445
See "Adding Results" tab for more information. |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Paste new data in row 50 and below. |  |  |  | OpenSimula V 0.5 | [5 empty] | University of Seville
Cells in blue are used in titles and labels |  |  |  | Program Version Release Date: |  |  |  | 2025-05-01 |  | Modeler Organization for Tables and Charts (short): |  |  |  | US
Editing them here flows thru to other tabs |  |  |  | Program Name for Tables and Charts (short): |  |  |  | OpenSimula
To print pdf file, see instructions on "Read Me" tab. |  |  |  | Results Submission Date: |  |  |  | 2025-03-14 |  | Model / Organization Indentifier for Charts (short): |  |  |  | OpenSimula/US | defaults to short program name / short organization name
Content Instructions
1. Use specified units
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| C61...J63: | Coil Loads, Fan Coil Air System, AE100 Series Cases
| S61...Y75: | Detailed Outputs, Fan Coil Air System, AE100 Series Cases
| C89...J95: | Coil Loads, Single Zone Air System, AE200 Series Cases
| S89...Z123: | Detailed Outputs, Single Zone Air System, AE200 Series Cases
| C137...O143: | Coil Loads, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| S137...AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| C185...O191: | Coil Loads, Variable Air Volume Air System, AE400 Series Cases
| S185...AC219: | Detailed Outputs, Variable Air Volume Air System, AE400 Series Cases
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | OpenSimula
| Version: | 0.5
| Date: | 2025-10-01
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 3.0218 | 0 | 0 | 8.3512 | 0 | 0 | 0 | 6.5846 | [6 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.3977 | 29.6115 | 29.6115 | 30.2197 | 21.0963 | 21.0963
| AE103 | 0 | 1.4492 | 0.58604 | 0 | 0.75637 | 0 | 0.75637 | 32.708 | [7 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0016825 | 0.0016828 | 0.0016828 | 0.0016828 | 0.0023946 | 0.0023946
| AE104 | 0 | 2.9342 | 0.58692 | 0 | 3.4804 | 2.2289 | 5.7093 | 98.4406 | [7 empty] | Specific volume (L/kgda) | 691.9366 | 788.3876 | 860.0088 | 860.0088 | 861.7364 | 836.7752 | 836.7752
[17 empty] | Enthalpy (J/gda) | -28.5404 | 8.6458 | 34.0904 | 34.0904 | 34.7042 | 27.3059 | 27.3059
[17 empty] | Mass flow rate (kgda/s) | 0.10975 | 0.32924 | 0.32924 | 0.32924 | 0.32924 | n/a* | 0.2195
[16 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7225 | 18.5138 | 18.5138 | 19.1021 | 23.3337 | 23.3337
[17 empty] | Humidity ratio (g/gda) | 0.0029317 | 0.00431 | 0.0043099 | 0.0043099 | 0.0043099 | 0.0049983 | 0.0049983
[17 empty] | Specific volume (L/kgda) | 821.5666 | 838.2761 | 831.9756 | 831.9756 | 833.6536 | 846.654 | 846.654
[17 empty] | Enthalpy (J/gda) | 23.0097 | 31.7924 | 29.5525 | 29.5525 | 30.149 | 36.1914 | 36.1914
[17 empty] | Mass flow rate (kgda/s) | 0.11347 | 0.34041 | 0.34041 | 0.34041 | 0.34041 | n/a* | 0.22694
[16 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8923 | 14.7579 | 14.7579 | 15.3445 | 23.8884 | 23.8884
[17 empty] | Humidity ratio (g/gda) | 0.016766 | 0.012924 | 0.010314 | 0.010314 | 0.010314 | 0.011001 | 0.011001
[17 empty] | Specific volume (L/kgda) | 872.9203 | 861.8645 | 829.1348 | 829.1348 | 830.8241 | 856.3597 | 856.3597
[17 empty] | Enthalpy (J/gda) | 69.831 | 57.9634 | 40.9239 | 40.9239 | 41.5253 | 52.0343 | 52.0343
[17 empty] | Mass flow rate (kgda/s) | 0.11379 | 0.34138 | 0.34138 | 0.34138 | 0.34138 | n/a* | 0.22759
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 3.0218 | 0 | 0 | 8.2807 | 0 | 0 | 0 | 6.5861 | [6 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6006 | 29.6167 | 29.6167 | 30.2253 | 21.0964 | 21.0964 | 21.4007
| AE203 | 0 | 1.4491 | 0.58604 | 0 | 0.82412 | 0 | 0.82412 | 32.7215 | [7 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0016836 | 0.0016836 | 0.0016836 | 0.0016836 | 0.002396 | 0.002396 | 0.002396
| AE204 | 0 | 2.9342 | 0.58677 | 0 | 3.5473 | 2.2295 | 5.7769 | 98.4144 | [7 empty] | Specific volume (L/kgda) | 691.9366 | 788.9653 | 860.0249 | 860.0249 | 861.7537 | 836.7771 | 836.7771 | 837.6425
| AE205 | 0 | 1.4652 | 0.5861 | 0 | 1.9123 | 0 | 1.9123 | 44.5287 | [7 empty] | Enthalpy (J/gda) | -28.5404 | 8.8533 | 34.098 | 34.098 | 34.7121 | 27.3093 | 27.3093 | 27.6167
| AE206 | 0 | 1.4626 | 0.5866 |  | 1.6937 | 1.0522 | 2.7459 | 99.4607 | [7 empty] | Mass flow rate (kgda/s) | 0.10968 | 0.32904 | 0.32904 | 0.32904 | 0.32904 | n/a* | 0.21936 | 0.21936
| AE226 | 0 | 1.4626 | 0.58608 | 0 | 1.5516 | 1.995 | 3.5467 | 99.3617 | [6 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9187 | 18.5106 | 18.5106 | 19.0993 | 23.3337 | 23.3337 | 23.628
| AE245 | 0 | 1.4652 | 0.58608 | 0 | 2.2017 | 0 | 2.2017 | 34.1262 | [7 empty] | Humidity ratio (g/gda) | 0.0029317 | 0.0043106 | 0.0043109 | 0.0043109 | 0.0043109 | 0.0049997 | 0.0049997 | 0.0049997
[17 empty] | Specific volume (L/kgda) | 821.5666 | 838.8365 | 831.9676 | 831.9676 | 833.6467 | 846.6558 | 846.6558 | 847.4963
[17 empty] | Enthalpy (J/gda) | 23.0097 | 31.9927 | 29.5515 | 29.5515 | 30.1484 | 36.1949 | 36.1949 | 36.4937
[17 empty] | Mass flow rate (kgda/s) | 0.11339 | 0.34019 | 0.34019 | 0.34019 | 0.34019 | n/a* | 0.22679 | 0.22679
[16 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.088 | 14.7519 | 14.7519 | 15.3389 | 23.8885 | 23.8885 | 24.1819
[17 empty] | Humidity ratio (g/gda) | 0.016766 | 0.012919 | 0.010307 | 0.010307 | 0.010307 | 0.010995 | 0.010995 | 0.010995
[17 empty] | Specific volume (L/kgda) | 872.9203 | 862.4238 | 829.1088 | 829.1088 | 830.7992 | 856.3509 | 856.3509 | 857.197
[17 empty] | Enthalpy (J/gda) | 69.831 | 58.1527 | 40.9006 | 40.9006 | 41.5024 | 52.0177 | 52.0177 | 52.3189
[17 empty] | Mass flow rate (kgda/s) | 0.11372 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | n/a* | 0.22744 | 0.22744
[16 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0519 | 18.4556 | 18.4556 | 19.0451 | 23.3331 | 23.3331 | 23.6279
[17 empty] | Humidity ratio (g/gda) | 0.0044783 | 0.0058604 | 0.0058606 | 0.0058606 | 0.0058606 | 0.0065506 | 0.0065506 | 0.0065506
[17 empty] | Specific volume (L/kgda) | 850.4208 | 849.8719 | 833.8691 | 833.8691 | 835.555 | 848.7486 | 848.7486 | 849.5924
[17 empty] | Enthalpy (J/gda) | 36.457 | 39.1152 | 33.425 | 33.425 | 34.0245 | 40.1404 | 40.1404 | 40.4405
[17 empty] | Mass flow rate (kgda/s) | 0.11322 | 0.33966 | 0.33966 | 0.33966 | 0.33966 | n/a* | 0.22644 | 0.22644
[16 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4208 | 18.406 | 18.406 | 19.0024 | 23.333 | 23.333 | 23.6313
[17 empty] | Humidity ratio (g/gda) | 0.01556 | 0.014455 | 0.013202 | 0.013202 | 0.013202 | 0.013901 | 0.013901 | 0.013901
[17 empty] | Specific volume (L/kgda) | 859.948 | 859.6779 | 843.4773 | 843.4773 | 845.2029 | 858.6748 | 858.6748 | 859.5385
[17 empty] | Enthalpy (J/gda) | 62.7193 | 60.3442 | 51.9878 | 51.9878 | 52.6025 | 58.843 | 58.843 | 59.1507
[17 empty] | Mass flow rate (kgda/s) | 0.11191 | 0.33573 | 0.33573 | 0.33573 | 0.33573 | n/a* | 0.22382 | 0.22382
[16 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 18.4044 | 18.4044 | 19.001 | 23.333 | 23.333 | 23.6313
[17 empty] | Humidity ratio (g/gda) | 0.01556 | 0.015565 | 0.013188 | 0.013188 | 0.013188 | 0.013886 | 0.013886 | 0.013886
[17 empty] | Specific volume (L/kgda) | 859.948 | 859.9545 | 843.4531 | 843.4531 | 845.1791 | 858.6542 | 858.6542 | 859.5182
[17 empty] | Enthalpy (J/gda) | 62.7193 | 62.7314 | 51.9487 | 51.9487 | 52.5636 | 58.8044 | 58.8044 | 59.1122
[17 empty] | Mass flow rate (kgda/s) | 0.33562 | 0.33562 | 0.33562 | 0.33562 | 0.33562 | n/a* | 0.22375 | 0.22375
[16 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 18.4523 | 18.4523 | 19.0423 | 23.333 | 23.333 | 23.628
[17 empty] | Humidity ratio (g/gda) | 0.0044783 | 0.0044808 | 0.0044807 | 0.0044807 | 0.0044807 | 0.0051711 | 0.0051711 | 0.0051711
[17 empty] | Specific volume (L/kgda) | 850.4208 | 850.4243 | 832.0271 | 832.0271 | 833.7103 | 846.8853 | 846.8853 | 847.7279
[17 empty] | Enthalpy (J/gda) | 36.457 | 36.4635 | 29.9232 | 29.9232 | 30.5216 | 36.6304 | 36.6304 | 36.9299
[17 empty] | Mass flow rate (kgda/s) | 0.33944 | 0.33944 | 0.33944 | 0.33944 | 0.33944 | n/a* | 0.2263 | 0.2263
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 |  | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) |  | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 3.0195 |  | 0 | 2.4354 | 0 | 0 | 3.7747 | 0 | 0 | 0 | 22.4118 | 7.7894 | 8.4642 |  | AE301 | Dry bulb temperature (°C) | -29 | 2.3528 | 7.2206 | 7.2206 | 7.7835 | 29.5476 | 28.0547 | 21.111 | 22.222 | 21.6665 | 21.9479
| AE303 | 0 | 1.449 | 0.67094 | 0 | 2.3271 | 0.97823 | 0 | 6.5489 | 0 | 6.5489 | 49.1748 | 2.245 | 2.4364 |  |  | Humidity ratio (g/gda) | 0.00025893 | 0.0014026 | 0.0014025 | 0.0014025 | 0.0014025 | 0.0014025 | 0.0014025 | 0.0020231 | 0.0022113 | 0.0021172 | 0.0021172
| AE304 | 0 | 2.9343 | 0.58634 | 0 | 3.5184 | 0.8795 | 0 | 9.8644 | 6.6051 | 16.4695 | 98.0574 | 0.84482 | 1.3315 |  |  | Specific volume (L/kgda) | 691.9366 | 782.2277 | 796.0486 | 796.0486 | 797.6468 | 859.4411 | 855.2023 | 836.3189 | 839.7298 | 838.0241 | 838.824
| AE305 | 0 | 1.4652 | 0.6403 | 0 | 2.3432 | 0.94248 | 0 | 9.1642 | 0 | 9.1642 | 66.2464 | 2.1752 | 2.351 |  |  | Enthalpy (J/gda) | -28.5404 | 5.881 | 10.7905 | 10.7905 | 11.3582 | 33.3097 | 31.8039 | 26.3768 | 27.9773 | 27.177 | 27.177
| AE306 | 0 | 1.4626 | 0.58588 | 0 | 2.3407 | 0.87896 | 0 | 8.5615 | 5.7668 | 14.3284 | 98.3662 | 2.1522 | 2.3206 |  |  | Mass flow rate (kgda/s) | 0.29647 | 0.77082 | 0.77082 | 0.77082 | 0.77082 | 0.35577 | 0.41506 | n/a* | n/a* | 0.47436 | 0.47436
| AE326 | 0 | 1.4626 | 0.58608 | 0 | 2.3407 | 0.8792 | 0 | 7.9955 | 12.7011 | 20.6966 | 97.9418 | 2.1398 | 2.3046 |  | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8393 | 12.2045 | 12.2045 | 12.78 | 19.1935 | 18.7458 | 23.333 | 24.444 | 23.8885 | 24.1762
| AE345 | 0 | 1.4652 | 0.58608 | 0 | 2.3432 | 0.8792 | 0 | 9.5012 | 0 | 9.5012 | 51.0089 | 2.1776 | 2.3541 |  |  | Humidity ratio (g/gda) | 0.0029317 | 0.0043206 | 0.0043208 | 0.0043208 | 0.0043208 | 0.0043208 | 0.0043208 | 0.0050918 | 0.0052843 | 0.0051881 | 0.0051881
[17 empty] | Specific volume (L/kgda) | 821.5666 | 838.6232 | 813.9923 | 813.9923 | 815.634 | 833.9289 | 832.6519 | 846.7782 | 850.2123 | 848.495 | 849.3169
[17 empty] | Enthalpy (J/gda) | 23.0097 | 31.9376 | 23.1822 | 23.1822 | 23.7658 | 30.2693 | 29.8154 | 36.4286 | 38.047 | 37.2377 | 37.2377
[17 empty] | Mass flow rate (kgda/s) | 0.28996 | 0.75391 | 0.75391 | 0.75391 | 0.75391 | 0.34796 | 0.40595 | n/a* | n/a* | 0.46395 | 0.46395
[16 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5711 | 12.1878 | 12.1878 | 12.78 | 15.2634 | 16.135 | 23.889 | 25 | 24.4445 | 24.7406
[17 empty] | Humidity ratio (g/gda) | 0.016766 | 0.012271 | 0.0086662 | 0.0086662 | 0.0086662 | 0.0086662 | 0.0086662 | 0.0093595 | 0.0095576 | 0.0094586 | 0.0094586
[17 empty] | Specific volume (L/kgda) | 872.9203 | 862.9387 | 819.5923 | 819.5923 | 821.2933 | 828.4265 | 830.9301 | 854.1403 | 857.604 | 855.8719 | 856.7234
[17 empty] | Enthalpy (J/gda) | 69.831 | 56.9979 | 34.1317 | 34.1317 | 34.737 | 37.2753 | 38.1662 | 47.8564 | 49.498 | 48.6771 | 48.6771
[17 empty] | Mass flow rate (kgda/s) | 0.28179 | 0.73267 | 0.73267 | 0.73267 | 0.73267 | 0.33816 | 0.39451 | n/a* | n/a* | 0.45088 | 0.45088
[16 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4572 | 12.196 | 12.196 | 12.78 | 19.0856 | 18.6216 | 23.333 | 24.444 | 23.8885 | 24.1805
[17 empty] | Humidity ratio (g/gda) | 0.0044783 | 0.0058314 | 0.0058316 | 0.0058316 | 0.0058316 | 0.0058316 | 0.0058316 | 0.0065783 | 0.0067736 | 0.0066759 | 0.0066759
[17 empty] | Specific volume (L/kgda) | 850.4208 | 850.9916 | 815.9317 | 815.9317 | 817.6016 | 835.6321 | 834.3055 | 848.7856 | 852.231 | 850.5081 | 851.3441
[17 empty] | Enthalpy (J/gda) | 36.457 | 39.4535 | 26.9864 | 26.9864 | 27.5803 | 33.9921 | 33.5203 | 40.2107 | 41.8395 | 41.025 | 41.025
[17 empty] | Mass flow rate (kgda/s) | 0.28575 | 0.74296 | 0.74296 | 0.74296 | 0.74296 | 0.3429 | 0.40005 | n/a* | n/a* | 0.45721 | 0.45721
[16 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7277 | 12.1919 | 12.1919 | 12.78 | 19.0631 | 18.5869 | 23.333 | 24.444 | 23.8885 | 24.1825
[17 empty] | Humidity ratio (g/gda) | 0.01556 | 0.011822 | 0.0086963 | 0.0086963 | 0.0086963 | 0.0086963 | 0.0086963 | 0.0093843 | 0.009581 | 0.0094826 | 0.0094826
[17 empty] | Specific volume (L/kgda) | 859.948 | 857.0064 | 819.6431 | 819.6431 | 821.3324 | 839.3805 | 838.0128 | 852.575 | 856.0364 | 854.3054 | 855.1511
[17 empty] | Enthalpy (J/gda) | 62.7193 | 53.9586 | 34.2117 | 34.2117 | 34.8128 | 41.2352 | 40.7485 | 47.3503 | 48.9883 | 48.1692 | 48.1692
[17 empty] | Mass flow rate (kgda/s) | 0.28374 | 0.73774 | 0.73774 | 0.73774 | 0.73774 | 0.3405 | 0.39724 | n/a* | n/a* | 0.454 | 0.454
[16 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 12.1899 | 12.1899 | 12.78 | 19.0484 | 18.5668 | 23.333 | 24.444 | 23.8885 | 24.1835
[17 empty] | Humidity ratio (g/gda) | 0.01556 | 0.015565 | 0.0086571 | 0.0086571 | 0.0086571 | 0.0086571 | 0.0086571 | 0.0093477 | 0.0095451 | 0.0094464 | 0.0094464
[17 empty] | Specific volume (L/kgda) | 859.948 | 859.9545 | 819.5863 | 819.5863 | 821.2814 | 839.2861 | 837.9028 | 852.5255 | 855.9877 | 854.2564 | 855.1049
[17 empty] | Enthalpy (J/gda) | 62.7193 | 62.7314 | 34.1106 | 34.1106 | 34.7138 | 41.1207 | 40.6285 | 47.2572 | 48.8968 | 48.0769 | 48.0769
[17 empty] | Mass flow rate (kgda/s) | 0.73521 | 0.73521 | 0.73521 | 0.73521 | 0.73521 | 0.33933 | 0.39588 | n/a* | n/a* | 0 | 0
[16 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 12.1964 | 12.1964 | 12.78 | 19.0884 | 18.6255 | 23.333 | 24.444 | 23.8885 | 24.1803
[17 empty] | Humidity ratio (g/gda) | 0.0044783 | 0.0044808 | 0.0044807 | 0.0044807 | 0.0044807 | 0.0044807 | 0.0044807 | 0.0051637 | 0.0053589 | 0.0052613 | 0.0052613
[17 empty] | Specific volume (L/kgda) | 850.4208 | 850.4243 | 814.177 | 814.177 | 815.8422 | 833.842 | 832.5212 | 846.8753 | 850.3134 | 848.5941 | 849.4276
[17 empty] | Enthalpy (J/gda) | 36.457 | 36.4635 | 23.5776 | 23.5776 | 24.1695 | 30.5684 | 30.0988 | 36.6115 | 38.2369 | 37.4241 | 37.4241
[17 empty] | Mass flow rate (kgda/s) | 0.74345 | 0.74345 | 0.74345 | 0.74345 | 0.74345 | 0.34313 | 0.40032 | n/a* | n/a* | 0 | 0
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 |  | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) |  | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | [14 empty] | AE401 | Dry bulb temperature (°C)
| AE403 | [15 empty] | Humidity ratio (g/gda)
| AE404 | [15 empty] | Specific volume (L/kgda)
| AE405 | [15 empty] | Enthalpy (J/gda)
| AE406 | [15 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
| AE426 | [14 empty] | AE403 | Dry bulb temperature (°C)
| AE445 | [15 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE404 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE405 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE406 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE426 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE445 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
* n/a = not applicable

## Title Page
ASHRAE Standard 140-2023 | To print example results:
Informative Annex B16, Section B16.7.2 | 1. Select results type in cell B21:
"Example" for Airside HVAC BESTEST Example Results
Example Results | "Comparison" if comparing new user results with the example results
for | 2. Select the following sheets:
Section 11, Airside HVAC Equipment Performance Tests AE301 through AE445 | "Title Page" thru "Figure List"
"Tables 1" thru "Delta Tables 2"
"Fig B16.7.2-1 TotalCoil" through "Fig B16.7.2-35 VAV dEcono"
3. Print, or Save to pdf.
The title page, and table and chart titles are based upon the selected results type,
and for comparison results, also include inputs from the program
information block of the "YourData" tab.
Results Type (Example or Comparison)
Example
Scratch area for Table Title
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.2
Scratch area for Table subtitle 1
Example Results for Section 11, Airside HVAC BESTEST Cases AE301 through AE445
Scratch area for Table subtitle 2
Scratch area for chart subtitles 1
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.2
Scratch area for chart subtitles 2
Example Results for Section 11, Airside HVAC BESTEST Cases AE301 through AE445

## Program List
ASHRAE Standard 140-2023
Computer Programs, Program Authors, and Producers of Example Results for
Section 11, Airside HVAC Equipment Performance Tests AE301 through AE445
The quasi-analytical solution and programs used to generate the example results are described in Table B17-13. The first
column of the table ("Model") indicates the program name and version number, or indicates a quasi-analytical solution.
The second column ("Authoring Organization") indicates the national research facility, university, or industry organization
with expertise in building science that wrote the simulation software.
The third column ("Implemented By") indicates the national research facility, university, or industry organization with
expertise in building science that performed the simulations or did the quasi-analytical solutions. The organizations that
performed simulations either ran software written by their organization or otherwise maintained contact with the program
authors during the project.
The fourth column ("Abbreviation") indicates the identifying abbreviation used in the results tables and figures.
See Standard 140, Informative Annex B17 for further details.
Table B17-13 Airside HVAC Cases
Participating Organizations and Models
Model | Authoring Organization | Implemented by | Abbreviation
Quasi-Analytical Solution (QAS) | PSUa/UNOb/TAMUc/NRELd/JNAe/ MDKf, United States | NRELd/JNAe/MDKf, United States | QAS/PSU-TAMU-NREL
DEEAPg 1.1.2 | AAON, Inc., United States | AAON, Inc., United States | DEEAP/AAON
DeSTh 2 | Tsinghua University, China | Tsinghua University, China / LBNLi, United States | DeST/TsinghuaU-LBNL
DOE-2.2 V48L | JJHj/LBNLi/UCk, United States | NRELd/JNAe/MDKf, United States | DOE-2.2/NREL
EnergyPlus 8.2.0 | DOE-BTl, United States | GARD Analytics, Inc., United States | EnergyPlus/GARD
IES-VEm 2014.2 | IESn, United Kingdom | IESn, United Kingdom | IES-VE/IES
LCEMo 3.10 | MLITp, Japan | TTEq, Japan | LCEM/MLIT-TTE
TRNSYS 17.01.0028 | TESSr/UWMs, United States | TESSr, United States | TRNSYS/TESS
a PSU: The Pennsylvania State University, United States
b UNO: University of Nebraska - Omaha, United States
c TAMU: Texas A&M University, United States
d NREL: National Renewable Energy Laboratory, United States
e JNA: J. Neymark & Associates, United States
f MDK: Mike D. Kennedy, Inc., United States
g DEEAP: Detailed Energy and Economic Analysis Program
h DeST: Designer's Simulation Toolkit
i LBNL: Lawrence Berkeley National Laboratory, United States
J JJH: James J. Hirsch & Associates, United States
k UC: University of California, United States
l DOE-BT: U.S. Department of Energy, Office of Building Technologies, Energy Efficiency and Renewable Energy, United States
m IES-VE: Integrated Environmental Solutions - Virtual Environment
n IES: Integrated Environmental Solutions, United Kingdom
o LCEM: Life Cycle Energy Management tool. LCEM results were only generated for the FC and SZ system cases (see Informative Annex B16,
Section B16.7.1); there are no LCEM results for the CV and VAV system cases (see Informative Annex B16, Section B16.7.2).
p MLIT: Ministry of Land, Infrastructure, Transportation and Tourism, Japan
q TTE: Takasago Thermal Engineering, Japan
r TESS: Thermal Energy System Specialists, United States
s UWM: University of Wisconsin - Madison, United States

## Table List
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.2
Example Results for Section 11, Airside HVAC BESTEST Cases AE301 through AE445
List of Tables
| Table | Description | Sheet Tab | Cell Range
| B16.7.2-1 | CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent (kWh/h) | Tables 1 | A5–J21
| B16.7.2-2 | CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h) |  | A24–J40
| B16.7.2-3 | CV/VAV Pre-Heating Coil Load [QHpreheat] (kWh/h) |  | A43–J59
| B16.7.2-4 | CV/VAV Total Cooling Coil Load [QCtotal] (kWh/h) |  | A62–J78
| B16.7.2-5 | CV/VAV Sensible Cooling Coil Load [QCsensible] (kWh/h) |  | A81–J97
| B16.7.2-6 | CV/VAV Latent Cooling Coil Load [QClatent] (kWh/h) |  | A100–J116
| B16.7.2-7 | CV/VAV Zone 1 Reheat Coil Load [QH1reheat] (kWh/h) |  | A119–J135
| B16.7.2-8 | CV/VAV Zone 2 Reheat Coil Load [QH2reheat] (kWh/h) |  | A138–J154
| B16.7.2-9 | CV/VAV Outdoor Air Temperature (°F) |  | A157–J173
| B16.7.2-10 | CV/VAV Outdoor Air Humidity Ratio (g/gda) |  | A176–J192
| B16.7.2-11 | CV/VAV Outdoor Air Mass Flow Rate (kgda/s) |  | A195–J211
| B16.7.2-12 | CV/VAV Cooling Coil Outlet Air Temperature (°C) |  | A214–J230
| B16.7.2-13 | CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] (%) |  | A233–J249
| B16.7.2-14 | CV/VAV Supply Fan Air Temperature Rise (°C) |  | A252–J268
| B16.7.2-15 | CV/VAV Supply Air Temperature (°C) |  | A271–J287
| B16.7.2-16 | CV/VAV Supply Air Humidity Ratio (g/gda) |  | A290–J306
| B16.7.2-17 | CV/VAV Supply Air Specific Volume (L/kgda) |  | A309–J325
| B16.7.2-18 | CV/VAV Supply Air Enthalpy (J/gda) |  | A328–J344
| B16.7.2-19 | CV/VAV Supply Air Mass Flow Rate (kgda/s) |  | A347–J363
| B16.7.2-20 | CV/VAV Ratio of Outdoor Air Mass Flow to Supply Air Mass Flow (fraction) |  | A366–J382
| B16.7.2-21 | CV/VAV Zone 1 Supply Air Temperature (°C) |  | A385–J401
| B16.7.2-22 | CV/VAV Zone 1 Air Temperature (°C) |  | A404–J420
| B16.7.2-23 | CV/VAV Zone 1 Humidity Ratio (g/gda) |  | A423–J439
| B16.7.2-24 | CV/VAV Zone 2 Supply Air Temperature (°C) |  | A442–J458
| B16.7.2-25 | CV/VAV Zone 2 Air Temperature (°C) |  | A461–J477
| B16.7.2-26 | CV/VAV Zone 2 Humidity Ratio (g/gda) |  | A480–J496
| B16.7.2-27 | CV/VAV Moisture Added to Zone 1 by Latent Gains (g/s) |  | A499–J516
| B16.7.2-28 | CV/VAV Moisture Added to Zone 2 by Latent Gains (g/s) |  | A518–J535
| B16.7.2-29 | CV/VAV Return Fan Air Temperature Rise (°C) |  | A537–J553
| B16.7.2-30 | CV/VAV Delta Preheat Coil Load, CV - VAV (kWh/h) | Delta Tables 1 | A5–J14
| B16.7.2-31 | CV/VAV Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) |  | A17–J26
| B16.7.2-32 | CV/VAV Delta Latent Cooling Coil Load, CV - VAV (kWh/h) |  | A29–J38
| B16.7.2-33 | CV/VAV Delta Total Cooling Coil Load, CV - VAV (kWh/h) |  | A41–J50
| B16.7.2-34 | CV Delta Cooling Coil Load, Economizer Operation (kWh/h) | Delta Tables 2 | A5–K13
| B16.7.2-35 | VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) |  | A16–K24

## Figure List
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.2
Example Results for Section 11, Airside HVAC BESTEST Cases AE301 through AE445
List of Figures
| Figure | Description | Sheet Tab
| B16.7.2-1 | CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent | Fig B16.7.2-1 TotalCoil H+C
| B16.7.2-2 | CV/VAV Total Sensible Coil Load, Heating + Cooling | Fig B16.7.2-2 TotalSensCoil H+C
| B16.7.2-3 | CV/VAV Pre-Heating Coil Load [QHpreheat] | Fig B16.7.2-3 PreHeatCoil
| B16.7.2-4 | CV/VAV Cooling Coil Load, Total [QCtotal] | Fig B16.7.2-4 CoolCoilTot
| B16.7.2-5 | CV/VAV Cooling Coil Load, Sensible [QCsensible] | Fig B16.7.2-5 CoolCoilSens
| B16.7.2-6 | CV/VAV Cooling Coil Load, Latent [QClatent] | Fig B16.7.2-6 CoolCoilLat
| B16.7.2-7 | CV/VAV Zone 1 Reheat Load [QH1reheat] | Fig B16.7.2-7 Zone1 Reheat
| B16.7.2-8 | CV/VAV Zone 2 Reheat Load [QH2reheat] | Fig B16.7.2-8 Zone2 Reheat
| B16.7.2-9 | CV/VAV Outdoor Air Temperature | Fig B16.7.2-9 OAT
| B16.7.2-10 | CV/VAV Outdoor Air Humidity Ratio | Fig B16.7.2-10 OAW
| B16.7.2-11 | CV/VAV Outdoor Air Mass Flow Rate | Fig B16.7.2-11 OAmassflow
| B16.7.2-12 | CV/VAV Cooling Coil Outlet Air Temperature | Fig B16.7.2-12 CCOT
| B16.7.2-13 | CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] | Fig B16.7.2-13 RHcco
| B16.7.2-14 | CV/VAV Supply Fan Air Temperature Rise | Fig B16.7.2-14 Supply Fan dT
| B16.7.2-15 | CV/VAV Supply Air Temperature | Fig B16.7.2-15 SAT
| B16.7.2-16 | CV/VAV Supply Air Humidity Ratio | Fig B16.7.2-16 SAW
| B16.7.2-17 | CV/VAV Supply Air Specific Volume | Fig B16.7.2-17 SAVs
| B16.7.2-18 | CV/VAV Supply Air Enthalpy | Fig B16.7.2-18 SAenth
| B16.7.2-19 | CV/VAV Supply Air Mass Flow Rate | Fig B16.7.2-19 SAmassflow
| B16.7.2-20 | CV/VAV Outdoor Air to Supply Air Mass Flow Ratio | Fig B16.7.2-20 OAfrac
| B16.7.2-21 | CV/VAV Zone 1 Supply Air Temperature | Fig B16.7.2-21 Zone1 SAT
| B16.7.2-22 | CV/VAV Zone 1 Air Temperature | Fig B16.7.2-22 Zone1 AirT
| B16.7.2-23 | CV/VAV Zone 1 Humidity Ratio | Fig B16.7.2-23 Zone1 AirW
| B16.7.2-24 | CV/VAV Zone 2 Supply Air Temperature | Fig B16.7.2-24 Zone2 SAT
| B16.7.2-25 | CV/VAV Zone 2 Air Temperature | Fig B16.7.2-25 Zone2 AirT
| B16.7.2-26 | CV/VAV Zone 2 Humidity Ratio | Fig B16.7.2-26 Zone2 AirW
| B16.7.2-27 | CV/VAV Moisture Added to Zone 1 by Latent Gains | Fig B16.7.2-27 Zone1 Lat Gain
| B16.7.2-28 | CV/VAV Moisture Added to Zone 2 by Latent Gains | Fig B16.7.2-28 Zone2 Lat Gain
| B16.7.2-29 | CV/VAV Return Fan Air Temperature Rise | Fig B16.7.2-29 Return Fan dT
| B16.7.2-30 | CV/VAV Delta Pre-Heating Coil Load, CV-VAV | Fig B16.7.2-30 CV-VV dPreheat
| B16.7.2-31 | CV/VAV Delta Total Cooling Coil Load, CV-VAV | Fig B16.7.2-31 CV-VV dTot Cool
| B16.7.2-32 | CV/VAV Delta Sensible Cooling Coil Load, CV-VAV | Fig B16.7.2-32 CV-VV dSens Cool
| B16.7.2-33 | CV/VAV Delta Latent Cooling Coil Load, CV-VAV | Fig B16.7.2-33 CV-VV dLat Cool
| B16.7.2-34 | CV Delta Cooling Coil Load, Economizer Operation | Fig B16.7.2-34 CV dEcono
| B16.7.2-35 | VAV Delta Cooling Coil Load, Economizer Operation | Fig B16.7.2-35 VAV dEcono

## scrape titles new new (hidden)
Org Tab Name | Org Chart Title | Org Yaxis Title | Proposed Num | New Tab Name | New Chart Title | New Axis Title
Fig 4.2-1 TotalCoil H+C | Figure 4.2-1. CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent | Coil Load (kWh/h) | 1 | Fig 4.2-1 TotalCoil H+C | Figure 4.2-1. CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-1 | CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent
Fig 4.2-2 TotalSensCoil H+C | Figure 4.2-2. CV/VAV Total Sensible Coil Load, Heating + Cooling | Coil Load (kWh/h) | 2 | Fig 4.2-2 TotalSensCoil H+C | Figure 4.2-2. CV/VAV Total Sensible Coil Load, Heating + Cooling | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-2 | CV/VAV Total Sensible Coil Load, Heating + Cooling
Fig 4.2-3 PreHeatCoil | Figure 4.2-3. CV/VAV Pre-Heating Coil Load [QHpreheat] | Coil Load (kWh/h) | 3 | Fig 4.2-3 PreHeatCoil | Figure 4.2-3. CV/VAV Pre-Heating Coil Load [QHpreheat] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-3 | CV/VAV Pre-Heating Coil Load [QHpreheat]
Fig 4.2-4 CoolCoilTot | Figure 4.2-4. CV/VAV Cooling Coil Load, Total [QCtotal] | Coil Load (kWh/h) | 4 | Fig 4.2-4 CoolCoilTot | Figure 4.2-4. CV/VAV Cooling Coil Load, Total [QCtotal] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-4 | CV/VAV Cooling Coil Load, Total [QCtotal]
Fig 4.2-5 CoolCoilSens | Figure 4.2-5. CV/VAV Cooling Coil Load, Sensible [QCsensible] | Coil Load (kWh/h) | 5 | Fig 4.2-5 CoolCoilSens | Figure 4.2-5. CV/VAV Cooling Coil Load, Sensible [QCsensible] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-5 | CV/VAV Cooling Coil Load, Sensible [QCsensible]
Fig 4.2-6 CoolCoilLat | Figure 4.2-6. CV/VAV Cooling Coil Load, Latent [QClatent] | Coil Load (kWh/h) | 6 | Fig 4.2-6 CoolCoilLat | Figure 4.2-6. CV/VAV Cooling Coil Load, Latent [QClatent] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-6 | CV/VAV Cooling Coil Load, Latent [QClatent]
Fig 4.2-7 Zone1 Reheat | Figure 4.2-7. CV/VAV Zone 1 Reheat Load [QH1reheat] | Coil Load (kWh/h) | 7 | Fig 4.2-7 Zone1 Reheat | Figure 4.2-7. CV/VAV Zone 1 Reheat Load [QH1reheat] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-7 | CV/VAV Zone 1 Reheat Load [QH1reheat]
Fig 4.2-8 Zone2 Reheat | Figure 4.2-8. CV/VAV Zone 2 Reheat Load [QH2reheat] | Coil Load (kWh/h) | 8 | Fig 4.2-8 Zone2 Reheat | Figure 4.2-8. CV/VAV Zone 2 Reheat Load [QH2reheat] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-8 | CV/VAV Zone 2 Reheat Load [QH2reheat]
Fig 4.2-9 OAT | Figure 4.2-9. CV/VAV Outdoor Air Temperature | Humidity Ratio (g/gda) | 9 | Fig 4.2-9 OAT | Figure 4.2-9. CV/VAV Outdoor Air Temperature | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.2-9 | CV/VAV Outdoor Air Temperature
Fig 4.2-10 OAW | Figure 4.2-10. CV/VAV Outdoor Air Humidity Ratio | Humidity Ratio (g/gda) | 10 | Fig 4.2-10 OAW | Figure 4.2-10. CV/VAV Outdoor Air Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.2-10 | CV/VAV Outdoor Air Humidity Ratio
Fig 4.2-11 OAmassflow | Figure 4.2-11. CV/VAV Outdoor Air Mass Flow Rate | Mass Flow Rate (kgda/s) | 11 | Fig 4.2-11 OAmassflow | Figure 4.2-11. CV/VAV Outdoor Air Mass Flow Rate | Mass Flow Rate (kgda/s) | TRUE | TRUE | TRUE | 4.2-11 | CV/VAV Outdoor Air Mass Flow Rate
Fig 4.2-12 CCOT | Figure 4.2-12. CV/VAV Cooling Coil Outlet Air Temperature | Temperature (°C) | 12 | Fig 4.2-12 CCOT | Figure 4.2-12. CV/VAV Cooling Coil Outlet Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-12 | CV/VAV Cooling Coil Outlet Air Temperature
Fig 4.2-13 RHcco | Figure 4.2-13. CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] | Relative Humidity (%) | 13 | Fig 4.2-13 RHcco | Figure 4.2-13. CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] | Relative Humidity (%) | TRUE | TRUE | TRUE | 4.2-13 | CV/VAV Cooling Coil Outlet Relative Humidity [RHcco]
Fig 4.2-14 Supply Fan dT | Figure 4.2-14. CV/VAV Supply Fan Air Temperature Rise | Temperature (°C) | 14 | Fig 4.2-14 Supply Fan dT | Figure 4.2-14. CV/VAV Supply Fan Air Temperature Rise | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-14 | CV/VAV Supply Fan Air Temperature Rise
Fig 4.2-15 SAT | Figure 4.2-15. CV/VAV Supply Air Temperature | Temperature (°C) | 15 | Fig 4.2-15 SAT | Figure 4.2-15. CV/VAV Supply Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-15 | CV/VAV Supply Air Temperature
Fig 4.2-16 SAW | Figure 4.2-16. CV/VAV Supply Air Humidity Ratio | Humidity Ratio (g/gda) | 16 | Fig 4.2-16 SAW | Figure 4.2-16. CV/VAV Supply Air Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.2-16 | CV/VAV Supply Air Humidity Ratio
Fig 4.2-17 SAVs | Figure 4.2-17. CV/VAV Supply Air Specific Volume | Specific Volume (L/kgda) | 17 | Fig 4.2-17 SAVs | Figure 4.2-17. CV/VAV Supply Air Specific Volume | Specific Volume (L/kgda) | TRUE | TRUE | TRUE | 4.2-17 | CV/VAV Supply Air Specific Volume
Fig 4.2-18 SAenth | Figure 4.2-18. CV/VAV Supply Air Enthalpy | Enthalpy (J/gda) | 18 | Fig 4.2-18 SAenth | Figure 4.2-18. CV/VAV Supply Air Enthalpy | Enthalpy (J/gda) | TRUE | TRUE | TRUE | 4.2-18 | CV/VAV Supply Air Enthalpy
Fig 4.2-19 SAmassflow | Figure 4.2-19. CV/VAV Supply Air Mass Flow Rate | Mass Flow Rate (kgda/s) | 19 | Fig 4.2-19 SAmassflow | Figure 4.2-19. CV/VAV Supply Air Mass Flow Rate | Mass Flow Rate (kgda/s) | TRUE | TRUE | TRUE | 4.2-19 | CV/VAV Supply Air Mass Flow Rate
Fig 4.2-20 Oafrac | Figure 4.2-20. CV/VAV Outdoor Air to Supply Air Mass Flow Ratio | Ratio (0 - 1) | 20 | Fig 4.2-20 Oafrac | Figure 4.2-20. CV/VAV Outdoor Air to Supply Air Mass Flow Ratio | Ratio (0 - 1) | TRUE | TRUE | TRUE | 4.2-20 | CV/VAV Outdoor Air to Supply Air Mass Flow Ratio
Fig 4.2-21 Zone1 SAT | Figure 4.2-21. CV/VAV Zone 1 Supply Air Temperature | Temperature (°C) | 21 | Fig 4.2-21 Zone1 SAT | Figure 4.2-21. CV/VAV Zone 1 Supply Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-21 | CV/VAV Zone 1 Supply Air Temperature
Fig 4.2-22 Zone1 AirT | Figure 4.2-22. CV/VAV Zone 1 Air Temperature | Temperature (°C) | 22 | Fig 4.2-22 Zone1 AirT | Figure 4.2-22. CV/VAV Zone 1 Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-22 | CV/VAV Zone 1 Air Temperature
Fig 4.2-23 Zone1 AirW | Figure 4.2-23. CV/VAV Zone 1 Humidity Ratio | Humidity Ratio (g/gda) | 23 | Fig 4.2-23 Zone1 AirW | Figure 4.2-23. CV/VAV Zone 1 Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.2-23 | CV/VAV Zone 1 Humidity Ratio
Fig 4.2-24 Zone2 SAT | Figure 4.2-24. CV/VAV Zone 2 Supply Air Temperature | Temperature (°C) | 24 | Fig 4.2-24 Zone2 SAT | Figure 4.2-24. CV/VAV Zone 2 Supply Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-24 | CV/VAV Zone 2 Supply Air Temperature
Fig 4.2-25 Zone2 AirT | Figure 4.2-25. CV/VAV Zone 2 Air Temperature | Temperature (°C) | 25 | Fig 4.2-25 Zone2 AirT | Figure 4.2-25. CV/VAV Zone 2 Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-25 | CV/VAV Zone 2 Air Temperature
Fig 4.2-26 Zone2 AirW | Figure 4.2-26. CV/VAV Zone 2 Humidity Ratio | Humidity Ratio (g/gda) | 26 | Fig 4.2-26 Zone2 AirW | Figure 4.2-26. CV/VAV Zone 2 Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.2-26 | CV/VAV Zone 2 Humidity Ratio
Fig 4.2-27 Zone1 Lat Gain | Figure 4.2-27. CV/VAV Moisture Added to Zone 1 by Latent Gains | Water Vapor (g/s) | 27 | Fig 4.2-27 Zone1 Lat Gain | Figure 4.2-27. CV/VAV Moisture Added to Zone 1 by Latent Gains | Water Vapor (g/s) | TRUE | TRUE | TRUE | 4.2-27 | CV/VAV Moisture Added to Zone 1 by Latent Gains
Fig 4.2-28 Zone2 Lat Gain | Figure 4.2-28. CV/VAV Moisture Added to Zone 2 by Latent Gains | Water Vapor (g/s) | 28 | Fig 4.2-28 Zone2 Lat Gain | Figure 4.2-28. CV/VAV Moisture Added to Zone 2 by Latent Gains | Water Vapor (g/s) | TRUE | TRUE | TRUE | 4.2-28 | CV/VAV Moisture Added to Zone 2 by Latent Gains
Fig 4.2-29 Return Fan dT | Figure 4.2-29. CV/VAV Return Fan Air Temperature Rise | Temperature (°C) | 29 | Fig 4.2-29 Return Fan dT | Figure 4.2-29. CV/VAV Return Fan Air Temperature Rise | Temperature (°C) | TRUE | TRUE | TRUE | 4.2-29 | CV/VAV Return Fan Air Temperature Rise
Fig 4.2-30 CV-VV dPreheat | Figure 4.2-30. CV/VAV Delta Pre-Heating Coil Load, CV-VAV | Delta Coil Load (kWh/h) | 30 | Fig 4.2-30 CV-VV dPreheat | Figure 4.2-30. CV/VAV Delta Pre-Heating Coil Load, CV-VAV | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-30 | CV/VAV Delta Pre-Heating Coil Load, CV-VAV
Fig 4.2-31 CV-VV dTot Cool | Figure 4.2-31. CV/VAV Delta Total Cooling Coil Load, CV-VAV | Delta Coil Load (kWh/h) | 31 | Fig 4.2-31 CV-VV dTot Cool | Figure 4.2-31. CV/VAV Delta Total Cooling Coil Load, CV-VAV | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-31 | CV/VAV Delta Total Cooling Coil Load, CV-VAV
Fig 4.2-32 CV-VV dSens Cool | Figure 4.2-32. CV/VAV Delta Sensible Cooling Coil Load, CV-VAV | Delta Coil Load (kWh/h) | 32 | Fig 4.2-32 CV-VV dSens Cool | Figure 4.2-32. CV/VAV Delta Sensible Cooling Coil Load, CV-VAV | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-32 | CV/VAV Delta Sensible Cooling Coil Load, CV-VAV
Fig 4.2-33 CV-VV dLat Cool | Figure 4.2-33. CV/VAV Delta Latent Cooling Coil Load, CV-VAV | Delta Coil Load (kWh/h) | 33 | Fig 4.2-33 CV-VV dLat Cool | Figure 4.2-33. CV/VAV Delta Latent Cooling Coil Load, CV-VAV | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-33 | CV/VAV Delta Latent Cooling Coil Load, CV-VAV
Fig 4.2-34 CV dEcono | Figure 4.2-34. CV Delta Cooling Coil Load, Economizer Operation | Delta Coil Load (kWh/h) | 34 | Fig 4.2-34 CV dEcono | Figure 4.2-34. CV Delta Cooling Coil Load, Economizer Operation | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-34 | CV Delta Cooling Coil Load, Economizer Operation
Fig 4.2-35 VAV dEcono | Figure 4.2-35. VAV Delta Cooling Coil Load, Economizer Operation | Delta Coil Load (kWh/h) | 35 | Fig 4.2-35 VAV dEcono | Figure 4.2-35. VAV Delta Cooling Coil Load, Economizer Operation | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.2-35 | VAV Delta Cooling Coil Load, Economizer Operation
=CONCATENATE("Figure 4.2-",D36,". Airside HVAC, ",MID(B36,FIND("VAV",B36,8),100))

## scrape titles new (hidden)
Org Name | New Title | Yaxis Title | Proposed Num | New Name | New Title | New Axis title
Fig 4-1 TotalCoil | Figure 4-1. Airside HVAC: Total Coil Load | Total Coil Load (kWh/h) | 18 | Fig 4-18 TotalCoil | Figure 4-18. Airside HVAC - CV/VAV: Total Coil Load | Total Coil Load (kWh/h)
Fig 4-2 TotalSensCoil | Figure 4-2. Airside HVAC: Total Sensible Coil Load | Total Sensible Coil Load (kWh/h) | 19 | Fig 4-19 TotalSensCoil | Figure 4-19. Airside HVAC - CV/VAV: Total Sensible Coil Load | Total Sensible Coil Load (kWh/h)
Fig 4-3 PreHeatCoilkWh | Figure 4-3. Airside HVAC: Pre-Heating Coil Load | Pre-Heating Coil Load (QHpreheat) (kWh/h) | 20 | Fig 4-20 PreHeatCoilkWh | Figure 4-20. Airside HVAC - CV/VAV: Pre-Heating Coil Load | Pre-Heating Coil Load (QHpreheat) (kWh/h)
Fig 4-4 CoolCoilTot | Figure 4-4. Airside HVAC: Cooling Coil Loads, Total | Cooling Coil Loads, Total (QCtotal) (kWh/h) | 21 | Fig 4-21 CoolCoilTot | Figure 4-21. Airside HVAC - CV/VAV: Cooling Coil Loads, Total | Cooling Coil Loads, Total (QCtotal) (kWh/h)
Fig 4-5 CoolCoilSens | Figure 4-5. Airside HVAC: Cooling Coil Loads, Sensible | Cooling Coil Loads, Sensible (QCsensible) (kWh/h) | 22 | Fig 4-22 CoolCoilSens | Figure 4-22. Airside HVAC - CV/VAV: Cooling Coil Loads, Sensible | Cooling Coil Loads, Sensible (QCsensible) (kWh/h)
Fig 4-6 CoolCoilLat | Figure 4-6. Airside HVAC: Cooling Coil Loads, Latent | Cooling Coil Loads, Latent (QClatent) (kWh/h) | 23 | Fig 4-23 CoolCoilLat | Figure 4-23. Airside HVAC - CV/VAV: Cooling Coil Loads, Latent | Cooling Coil Loads, Latent (QClatent) (kWh/h)
Fig 4-7 RHcco | Figure 4-7. Airside HVAC: Cooling Coil Outlet Relative Humidity | Cooling Coil Outlet Relative Humidity (RHcco) (%) | 24 | Fig 4-24 RHcco | Figure 4-24. Airside HVAC - CV/VAV: Cooling Coil Outlet Relative Humidity | Cooling Coil Outlet Relative Humidity (RHcco) (%)
Fig 4-8 Z1 Reheat | Figure 4-8. Airside HVAC: Zone 1 Reheat Load | Zone 1 Reheat Load (QH1reheat) (kWh/h) | 25 | Fig 4-25 Z1 Reheat | Figure 4-25. Airside HVAC - CV/VAV: Zone 1 Reheat Load | Zone 1 Reheat Load (QH1reheat) (kWh/h)
Fig 4-9 Z2 Reheat | Figure 4-9. Airside HVAC: Zone 2 Reheat Load | Zone 2 Reheat Load (QH2reheat) (kWh/h) | 26 | Fig 4-26 Z2 Reheat | Figure 4-26. Airside HVAC - CV/VAV: Zone 2 Reheat Load | Zone 2 Reheat Load (QH2reheat) (kWh/h)
Fig 4-10 OAW | Figure 4-10. Airside HVAC: Outdoor Air Humidity Ratio | Outdoor Air Humidity Ratio (g/gda) | 27 | Fig 4-27 OAW | Figure 4-27. Airside HVAC - CV/VAV: Outdoor Air Humidity Ratio | Outdoor Air Humidity Ratio (g/gda)
Fig 4-11 OAmassflow | Figure 4-11. Airside HVAC: Outdoor Air Mass Flow Rate | Outdoor Air Mass Flow Rate (kgda/s) | 28 | Fig 4-28 OAmassflow | Figure 4-28. Airside HVAC - CV/VAV: Outdoor Air Mass Flow Rate | Outdoor Air Mass Flow Rate (kgda/s)
Fig 4-12 CCOT | Figure 4-12. Airside HVAC: Cooling Coil Outlet Air Temperature | Cooling Coil Outlet Air Temperature (°C) | 29 | Fig 4-29 CCOT | Figure 4-29. Airside HVAC - CV/VAV: Cooling Coil Outlet Air Temperature | Cooling Coil Outlet Air Temperature (°C)
Fig 4-13 SAT | Figure 4-13. Airside HVAC: Supply Air Temperature | Supply Air Temperature (°C) | 30 | Fig 4-30 SAT | Figure 4-30. Airside HVAC - CV/VAV: Supply Air Temperature | Supply Air Temperature (°C)
Fig 4-14 SAW | Figure 4-14. Airside HVAC: Supply Air Humidity Ratio | Supply Air Humidity Ratio (g/gda) | 31 | Fig 4-31 SAW | Figure 4-31. Airside HVAC - CV/VAV: Supply Air Humidity Ratio | Supply Air Humidity Ratio (g/gda)
Fig 4-15 SAVs | Figure 4-15. Airside HVAC: Supply Air Specific Volume | Supply Air Specific Volume (L/kgda) | 32 | Fig 4-32 SAVs | Figure 4-32. Airside HVAC - CV/VAV: Supply Air Specific Volume | Supply Air Specific Volume (L/kgda)
Fig 4-16 SAenth | Figure 4-16. Airside HVAC: Supply Air Enthalpy | Supply Air Enthalpy (j/gda) | 33 | Fig 4-33 SAenth | Figure 4-33. Airside HVAC - CV/VAV: Supply Air Enthalpy | Supply Air Enthalpy (j/gda)
Fig 4-17 SAmassflow | Figure 4-17. Airside HVAC: Supply Air Mass Flow Rate | Supply Air Mass Flow Rate (kgda/s) | 34 | Fig 4-34 SAmassflow | Figure 4-34. Airside HVAC - CV/VAV: Supply Air Mass Flow Rate | Supply Air Mass Flow Rate (kgda/s)
Fig 4-18 Supply Fan dT | Figure 4-18. Airside HVAC: Supply Fan Temperature Rise | Supply Fan Temperature Rise (°C) | 35 | Fig 4-35 Supply Fan dT | Figure 4-35. Airside HVAC - CV/VAV: Supply Fan Temperature Rise | Supply Fan Temperature Rise (°C)
Fig 4-19 Z1 AirTemp | Figure 4-19. Airside HVAC: Zone 1 Air Temperature | Zone 1 Air Temperature (°C) | 36 | Fig 4-36 Z1 AirTemp | Figure 4-36. Airside HVAC - CV/VAV: Zone 1 Air Temperature | Zone 1 Air Temperature (°C)
Fig 4-20 Z1 SAT | Figure 4-20. Airside HVAC: Zone 1 Supply Air Temperature | Zone 1 Supply Air Temperature (°C) | 37 | Fig 4-37 Z1 SAT | Figure 4-37. Airside HVAC - CV/VAV: Zone 1 Supply Air Temperature | Zone 1 Supply Air Temperature (°C)
Fig 4-21 Z1 delta W | Figure 4-21. Airside HVAC: Zone 1 Humidity Ratio Rise | Delta W (Zone 1 W minus SAW) | 38 | Fig 4-38 Z1 delta W | Figure 4-38. Airside HVAC - CV/VAV: Zone 1 Humidity Ratio Rise | Delta W (Zone 1 W minus SAW)
Fig 4-22 Z2 AirTemp | Figure 4-22. Airside HVAC: Zone 2 Air Temperature | Zone 2 Air Temperature (°C) | 39 | Fig 4-39 Z2 AirTemp | Figure 4-39. Airside HVAC - CV/VAV: Zone 2 Air Temperature | Zone 2 Air Temperature (°C)
Fig 4-23 Z2 SAT | Figure 4-23. Airside HVAC: Zone 2 Supply Air Temperature | Zone 2 Supply Air Temperature (°C) | 40 | Fig 4-40 Z2 SAT | Figure 4-40. Airside HVAC - CV/VAV: Zone 2 Supply Air Temperature | Zone 2 Supply Air Temperature (°C)
Fig 4-24 Z2 delta W | Figure 4-24. Airside HVAC: Zone 1 Humidity Ratio Rise | Delta W (Zone 2 W minus SAW) | 41 | Fig 4-41 Z2 delta W | Figure 4-41. Airside HVAC - CV/VAV: Zone 1 Humidity Ratio Rise | Delta W (Zone 2 W minus SAW)
Fig 4-25 Return Fan dT | Figure 4-25. Airside HVAC: Return Fan Temperature Rise | Return Fan Temperature Rise (°C) | 42 | Fig 4-42 Return Fan dT | Figure 4-42. Airside HVAC - CV/VAV: Return Fan Temperature Rise | Return Fan Temperature Rise (°C)
Fig 4-26 CV-VV dPreheat | Figure 4-26. Airside HVAC: Delta Pre-Heating Coil Load, CV-VAV | Delta Pre-Heating Coil Load (QHpreheat) (kWh/h) | 43 | Fig 4-43 CV-VV dPreheat | Figure 4-43. Airside HVAC - CV/VAV: Delta Pre-Heating Coil Load, CV-VAV | Delta Pre-Heating Coil Load (QHpreheat) (kWh/h)
Fig 4-27 CV-VV dTot Cool | Figure 4-27. Airside HVAC: Delta Total Cooling Coil Load, CV-VAV | Delta Cooling Coil Load, Total (QCtotal) (kWh/h) | 44 | Fig 4-44 CV-VV dTot Cool | Figure 4-44. Airside HVAC - CV/VAV: Delta Total Cooling Coil Load, CV-VAV | Delta Cooling Coil Load, Total (QCtotal) (kWh/h)
Fig 4-28 CV-VV dSens Cool | Figure 4-28. Airside HVAC: Delta Sensible Cooling Coil Load, CV-VAV | Delta Cooling Coil Load, Sensible (QCsensible) (kWh/h) | 45 | Fig 4-45 CV-VV dSens Cool | Figure 4-45. Airside HVAC - CV/VAV: Delta Sensible Cooling Coil Load, CV-VAV | Delta Cooling Coil Load, Sensible (QCsensible) (kWh/h)
Fig 4-29 CV-VV dLat Cool | Figure 4-29. Airside HVAC: Delta Latent Cooling Coil Load, CV-VAV | Delta Cooling Coil Load, Latent (QClatent) (kWh/h) | 46 | Fig 4-46 CV-VV dLat Cool | Figure 4-46. Airside HVAC - CV/VAV: Delta Latent Cooling Coil Load, CV-VAV | Delta Cooling Coil Load, Latent (QClatent) (kWh/h)
Fig 4-30 CV dEcono | Figure 4-30. Airside HVAC: Delta Cooling Coil Loads, Econo - No Econo | Delta Cooling Coil Load, Econo - No Econo (kWh/h) | 47 | Fig 4-47 CV dEcono | Figure 4-47. Airside HVAC - CV/VAV: Delta Cooling Coil Loads, Econo - No Econo | Delta Cooling Coil Load, Econo - No Econo (kWh/h)
Fig 4-31 VAV dEcono | Figure 4-31. Airside HVAC: Delta Cooling Coil Loads, Econo - No Econo | Delta Cooling Coil Load, Econo - No Econo (kWh/h) | 48 | Fig 4-48 VAV dEcono | Figure 4-48. Airside HVAC - CV/VAV: Delta Cooling Coil Loads, Econo - No Econo | Delta Cooling Coil Load, Econo - No Econo (kWh/h)

## scrape titles (hidden)
Org Name | Yaxis Title | Proposed Num | New root | New Name | New Title | New Axis title
TotalCoil (2) | Aggregate Coil Loads, Heating+Cooling (kWh/h) | 1 | TotalCoil | Fig 4-1 TotalCoil | Figure 4-1. Airside HVAC - CV/VAV: Aggregate Coil Loads, Heating+Cooling | Total Coil Load (kWh/h)
TotalSensCoil (2) | Aggregate Coil Loads, Heating+Cooling (kWh/h) | 2 | TotalSensCoil | Fig 4-2 TotalSensCoil | Figure 4-2. Airside HVAC: Aggregate Coil Loads, Heating+Cooling | Total Sensible Coil Load (kWh/h)
PreHeatCoilkWh (2) | Pre-Heating Coil Load (QHpreheat) (kWh/h) | 3 | PreHeatCoilkWh | Fig 4-3 PreHeatCoilkWh | Figure 4-3. Airside HVAC: Pre-Heating Coil Load | Pre-Heating Coil Load (QHpreheat) (kWh/h)
CoolCoilTot (2) | Cooling Coil Loads, Total (QCtotal) (kWh/h) | 4 | CoolCoilTot | Fig 4-4 CoolCoilTot | Figure 4-4. Airside HVAC: Cooling Coil Loads, Total | Cooling Coil Loads, Total (QCtotal) (kWh/h)
CoolCoilSens (2) | Cooling Coil Loads, Sensible (QCsensible) (kWh/h) | 5 | CoolCoilSens | Fig 4-5 CoolCoilSens | Figure 4-5. Airside HVAC: Cooling Coil Loads, Sensible | Cooling Coil Loads, Sensible (QCsensible) (kWh/h)
CoolCoilLat (2) | Cooling Coil Loads, Latent (QClatent) (kWh/h) | 6 | CoolCoilLat | Fig 4-6 CoolCoilLat | Figure 4-6. Airside HVAC: Cooling Coil Loads, Latent | Cooling Coil Loads, Latent (QClatent) (kWh/h)
RHcco (2) | Cooling Coil Outlet Relative Humidity (RHcco) (%) | 7 | RHcco | Fig 4-7 RHcco | Figure 4-7. Airside HVAC: Cooling Coil Outlet Relative Humidity | Cooling Coil Outlet Relative Humidity (RHcco) (%)
Z1 Reheat (2) | Zone 1 Reheat Load (QH1reheat) (kWh/h) | 8 | Z1 Reheat | Fig 4-8 Z1 Reheat | Figure 4-8. Airside HVAC: Zone 1 Reheat Load | Zone 1 Reheat Load (QH1reheat) (kWh/h)
Z2 Reheat (2) | Zone 2 Reheat Load (QH2reheat) (kWh/h) | 9 | Z2 Reheat | Fig 4-9 Z2 Reheat | Figure 4-9. Airside HVAC: Zone 2 Reheat Load | Zone 2 Reheat Load (QH2reheat) (kWh/h)
OAW (2) | Outdoor Air Humidity Ratio (g/gda) | 10 | OAW | Fig 4-10 OAW | Figure 4-10. Airside HVAC: Outdoor Air Humidity Ratio | Outdoor Air Humidity Ratio (g/gda)
OAmassflow (2) | Outdoor Air Mass Flow Rate (kgda/s) | 11 | OAmassflow | Fig 4-11 OAmassflow | Figure 4-11. Airside HVAC: Outdoor Air Mass Flow Rate | Outdoor Air Mass Flow Rate (kgda/s)
CCOT (2) | Cooling Coil Outlet Air Temperature (°C) | 12 | CCOT | Fig 4-12 CCOT | Figure 4-12. Airside HVAC: Cooling Coil Outlet Air Temperature | Cooling Coil Outlet Air Temperature (°C)
SAT (2) | Supply Air Temperature (°C) | 13 | SAT | Fig 4-13 SAT | Figure 4-13. Airside HVAC: Supply Air Temperature | Supply Air Temperature (°C)
SAW (2) | Supply Air Humidity Ratio (g/gda) | 14 | SAW | Fig 4-14 SAW | Figure 4-14. Airside HVAC: Supply Air Humidity Ratio | Supply Air Humidity Ratio (g/gda)
SAVs (2) | Supply Air Specific Volume (L/kgda) | 15 | SAVs | Fig 4-15 SAVs | Figure 4-15. Airside HVAC: Supply Air Specific Volume | Supply Air Specific Volume (L/kgda)
SAenth (2) | Supply Air Enthalpy (j/gda) | 16 | SAenth | Fig 4-16 SAenth | Figure 4-16. Airside HVAC: Supply Air Enthalpy | Supply Air Enthalpy (j/gda)
SAmassflow (2) | Supply Air Mass Flow Rate (kgda/s) | 17 | SAmassflow | Fig 4-17 SAmassflow | Figure 4-17. Airside HVAC: Supply Air Mass Flow Rate | Supply Air Mass Flow Rate (kgda/s)
Supply Fan dT (2) | Supply Fan Temperature Rise (°C) | 18 | Supply Fan dT | Fig 4-18 Supply Fan dT | Figure 4-18. Airside HVAC: Supply Fan Temperature Rise | Supply Fan Temperature Rise (°C)
Z1 AirTemp (2) | Zone 1 Air Temperature (°C) | 19 | Z1 AirTemp | Fig 4-19 Z1 AirTemp | Figure 4-19. Airside HVAC: Zone 1 Air Temperature | Zone 1 Air Temperature (°C)
Z1 SAT (2) | Zone 1 Supply Air Temperature (°C) | 20 | Z1 SAT | Fig 4-20 Z1 SAT | Figure 4-20. Airside HVAC: Zone 1 Supply Air Temperature | Zone 1 Supply Air Temperature (°C)
Z1 delta W (2) | Delta W (Zone 1 W minus SAW) | 21 | Z1 delta W | Fig 4-21 Z1 delta W | Figure 4-21. Airside HVAC: Delta W | Delta W (Zone 1 W minus SAW)
Z2 AirTemp (2) | Zone 2 Air Temperature (°C) | 22 | Z2 AirTemp | Fig 4-22 Z2 AirTemp | Figure 4-22. Airside HVAC: Zone 2 Air Temperature | Zone 2 Air Temperature (°C)
Z2 SAT (2) | Zone 2 Supply Air Temperature (°C) | 23 | Z2 SAT | Fig 4-23 Z2 SAT | Figure 4-23. Airside HVAC: Zone 2 Supply Air Temperature | Zone 2 Supply Air Temperature (°C)
Z2 delta W (2) | Delta W (Zone 2 W minus SAW) | 24 | Z2 delta W | Fig 4-24 Z2 delta W | Figure 4-24. Airside HVAC: Delta W | Delta W (Zone 2 W minus SAW)
Return Fan dT (2) | Return Fan Temperature Rise (°C) | 25 | Return Fan dT | Fig 4-25 Return Fan dT | Figure 4-25. Airside HVAC: Return Fan Temperature Rise | Return Fan Temperature Rise (°C)
CV-VV Delta Preheat (2) | CV - VAV Delta Pre-Heating Coil Load (QHpreheat) (kWh/h) | 26 | CV-VV dPreheat | Fig 4-26 CV-VV dPreheat | Figure 4-26. Airside HVAC: CV - VAV Delta Pre-Heating Coil Load | Delta Pre-Heating Coil Load (QHpreheat) (kWh/h)
CV-VV Delta Total Cooling (2) | CV - VAV Delta Cooling Coil Load, Total (QCtotal) (kWh/h) | 27 | CV-VV dTot Cool | Fig 4-27 CV-VV dTot Cool | Figure 4-27. Airside HVAC: CV - VAV Delta Cooling Coil Load, Total | Delta Cooling Coil Loads, Total (QCtotal) (kWh/h)
CV-VV Delta Sensible Coolin (2 | CV - VAV Delta Cooling Coil Load, Sensible (QCsensible) (kWh/h) | 28 | CV-VV dSens Cool | Fig 4-28 CV-VV dSens Cool | Figure 4-28. Airside HVAC: CV - VAV Delta Cooling Coil Load, Sensible | Delta Cooling Coil Loads, Sensible (QCsensible) (kWh/h)
CV-VV Delta Latent Cooling (2) | CV - VAV Delta Cooling Coil Load, Latent (QClatent) (kWh/h) | 29 | CV-VV dLat Cool | Fig 4-29 CV-VV dLat Cool | Figure 4-29. Airside HVAC: CV - VAV Delta Cooling Coil Load, Latent | Delta Cooling Coil Loads, Latent (QClatent) (kWh/h)
CV Delta Econo (2) | Economizer Delta Cooling Coil Load (kWh/h) | 30 | CV dEcono | Fig 4-30 CV dEcono | Figure 4-30. Airside HVAC: Economizer Delta Cooling Coil Load | Delta Cooling Coil Loads, Econo - No Econo (kWh/h)
VAV Delta Econo (2) | Economiser Delta Cooling Coil Load (kWh/h) | 31 | VAV dEcono | Fig 4-31 VAV dEcono | Figure 4-31. Airside HVAC: Economiser Delta Cooling Coil Load | Delta Cooling Coil Loads, Econo - No Econo (kWh/h)

## scrape Table names (hidden)
worksheet | Table Name | sequence | Table Name Root | New Table Name | number
Tables 1 | Table 4.2-1. CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent (kWh/h) | 1 | CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent (kWh/h) | Table 4.2-1. CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent (kWh/h) | 4.2-1 | TRUE
Tables 1 | Table 4.2-2. CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h) | 2 | CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h) | Table 4.2-2. CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h) | 4.2-2 | TRUE
Tables 1 | Table 4.2-3. CV/VAV Pre-Heating Coil Load [QHpreheat] (kWh/h) | 3 | CV/VAV Pre-Heating Coil Load [QHpreheat] (kWh/h) | Table 4.2-3. CV/VAV Pre-Heating Coil Load [QHpreheat] (kWh/h) | 4.2-3 | TRUE
Tables 1 | Table 4.2-4. CV/VAV Total Cooling Coil Load [QCtotal] (kWh/h) | 4 | CV/VAV Total Cooling Coil Load [QCtotal] (kWh/h) | Table 4.2-4. CV/VAV Total Cooling Coil Load [QCtotal] (kWh/h) | 4.2-4 | TRUE
Tables 1 | Table 4.2-5. CV/VAV Sensible Cooling Coil Load [QCsensible] (kWh/h) | 5 | CV/VAV Sensible Cooling Coil Load [QCsensible] (kWh/h) | Table 4.2-5. CV/VAV Sensible Cooling Coil Load [QCsensible] (kWh/h) | 4.2-5 | TRUE
Tables 1 | Table 4.2-6. CV/VAV Latent Cooling Coil Load [QClatent] (kWh/h) | 6 | CV/VAV Latent Cooling Coil Load [QClatent] (kWh/h) | Table 4.2-6. CV/VAV Latent Cooling Coil Load [QClatent] (kWh/h) | 4.2-6 | TRUE
Tables 1 | Table 4.2-7. CV/VAV Zone 1 Reheat Coil Load [QH1reheat] (kWh/h) | 7 | CV/VAV Zone 1 Reheat Coil Load [QH1reheat] (kWh/h) | Table 4.2-7. CV/VAV Zone 1 Reheat Coil Load [QH1reheat] (kWh/h) | 4.2-7 | TRUE
Tables 1 | Table 4.2-8. CV/VAV Zone 2 Reheat Coil Load [QH2reheat] (kWh/h) | 8 | CV/VAV Zone 2 Reheat Coil Load [QH2reheat] (kWh/h) | Table 4.2-8. CV/VAV Zone 2 Reheat Coil Load [QH2reheat] (kWh/h) | 4.2-8 | TRUE
Tables 1 | Table 4.2-9. CV/VAV Outdoor Air Temperature (°F) | 9 | CV/VAV Outdoor Air Temperature (°F) | Table 4.2-9. CV/VAV Outdoor Air Temperature (°F) | 4.2-9 | TRUE
Tables 1 | Table 4.2-10. CV/VAV Outdoor Air Humidity Ratio (g/gda) | 10 | CV/VAV Outdoor Air Humidity Ratio (g/gda) | Table 4.2-10. CV/VAV Outdoor Air Humidity Ratio (g/gda) | 4.2-10 | TRUE
Tables 1 | Table 4.2-11. CV/VAV Outdoor Air Mass Flow Rate (kgda/s) | 11 | CV/VAV Outdoor Air Mass Flow Rate (kgda/s) | Table 4.2-11. CV/VAV Outdoor Air Mass Flow Rate (kgda/s) | 4.2-11 | TRUE
Tables 1 | Table 4.2-12. CV/VAV Cooling Coil Outlet Air Temperature (°C) | 12 | CV/VAV Cooling Coil Outlet Air Temperature (°C) | Table 4.2-12. CV/VAV Cooling Coil Outlet Air Temperature (°C) | 4.2-12 | TRUE
Tables 1 | Table 4.2-13. CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] (%) | 13 | CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] (%) | Table 4.2-13. CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] (%) | 4.2-13 | TRUE
Tables 1 | Table 4.2-14. CV/VAV Supply Fan Air Temperature Rise (°C) | 14 | CV/VAV Supply Fan Air Temperature Rise (°C) | Table 4.2-14. CV/VAV Supply Fan Air Temperature Rise (°C) | 4.2-14 | TRUE
Tables 1 | Table 4.2-15. CV/VAV Supply Air Temperature (°C) | 15 | CV/VAV Supply Air Temperature (°C) | Table 4.2-15. CV/VAV Supply Air Temperature (°C) | 4.2-15 | TRUE
Tables 1 | Table 4.2-16. CV/VAV Supply Air Humidity Ratio (g/gda) | 16 | CV/VAV Supply Air Humidity Ratio (g/gda) | Table 4.2-16. CV/VAV Supply Air Humidity Ratio (g/gda) | 4.2-16 | TRUE
Tables 1 | Table 4.2-17. CV/VAV Supply Air Specific Volume (L/kgda) | 17 | CV/VAV Supply Air Specific Volume (L/kgda) | Table 4.2-17. CV/VAV Supply Air Specific Volume (L/kgda) | 4.2-17 | TRUE
Tables 1 | Table 4.2-18. CV/VAV Supply Air Enthalpy (J/gda) | 18 | CV/VAV Supply Air Enthalpy (J/gda) | Table 4.2-18. CV/VAV Supply Air Enthalpy (J/gda) | 4.2-18 | TRUE
Tables 1 | Table 4.2-19. CV/VAV Supply Air Mass Flow Rate (kgda/s) | 19 | CV/VAV Supply Air Mass Flow Rate (kgda/s) | Table 4.2-19. CV/VAV Supply Air Mass Flow Rate (kgda/s) | 4.2-19 | TRUE
Tables 1 | Table 4.2-20. CV/VAV Ratio of Outdoor Air Mass Flow to Supply Air Mass Flow (fraction) | 20 | CV/VAV Ratio of Outdoor Air Mass Flow to Supply Air Mass Flow (fraction) | Table 4.2-20. CV/VAV Ratio of Outdoor Air Mass Flow to Supply Air Mass Flow (fraction) | 4.2-20 | TRUE
Tables 1 | Table 4.2-21. CV/VAV Zone 1 Supply Air Temperature (°C) | 21 | CV/VAV Zone 1 Supply Air Temperature (°C) | Table 4.2-21. CV/VAV Zone 1 Supply Air Temperature (°C) | 4.2-21 | TRUE
Tables 1 | Table 4.2-22. CV/VAV Zone 1 Air Temperature (°C) | 22 | CV/VAV Zone 1 Air Temperature (°C) | Table 4.2-22. CV/VAV Zone 1 Air Temperature (°C) | 4.2-22 | TRUE
Tables 1 | Table 4.2-23. CV/VAV Zone 1 Humidity Ratio (g/gda) | 23 | CV/VAV Zone 1 Humidity Ratio (g/gda) | Table 4.2-23. CV/VAV Zone 1 Humidity Ratio (g/gda) | 4.2-23 | TRUE
Tables 1 | Table 4.2-24. CV/VAV Zone 2 Supply Air Temperature (°C) | 24 | CV/VAV Zone 2 Supply Air Temperature (°C) | Table 4.2-24. CV/VAV Zone 2 Supply Air Temperature (°C) | 4.2-24 | TRUE
Tables 1 | Table 4.2-25. CV/VAV Zone 2 Air Temperature (°C) | 25 | CV/VAV Zone 2 Air Temperature (°C) | Table 4.2-25. CV/VAV Zone 2 Air Temperature (°C) | 4.2-25 | TRUE
Tables 1 | Table 4.2-26. CV/VAV Zone 2 Humidity Ratio (g/gda) | 26 | CV/VAV Zone 2 Humidity Ratio (g/gda) | Table 4.2-26. CV/VAV Zone 2 Humidity Ratio (g/gda) | 4.2-26 | TRUE
Tables 1 | Table 4.2-27. CV/VAV Moisture Added to Zone 1 by Latent Gains (g/s) | 27 | CV/VAV Moisture Added to Zone 1 by Latent Gains (g/s) | Table 4.2-27. CV/VAV Moisture Added to Zone 1 by Latent Gains (g/s) | 4.2-27 | TRUE
Tables 1 | Table 4.2-28. CV/VAV Moisture Added to Zone 2 by Latent Gains (g/s) | 28 | CV/VAV Moisture Added to Zone 2 by Latent Gains (g/s) | Table 4.2-28. CV/VAV Moisture Added to Zone 2 by Latent Gains (g/s) | 4.2-28 | TRUE
Tables 1 | Table 4.2-29. CV/VAV Return Fan Air Temperature Rise (°C) | 29 | CV/VAV Return Fan Air Temperature Rise (°C) | Table 4.2-29. CV/VAV Return Fan Air Temperature Rise (°C) | 4.2-29 | TRUE
Delta Tables 1 | Table 4.2-30. CV/VAV Delta Preheat Coil Load, CV - VAV (kWh/h) | 30 | CV/VAV Delta Preheat Coil Load, CV - VAV (kWh/h) | Table 4.2-30. CV/VAV Delta Preheat Coil Load, CV - VAV (kWh/h) | 4.2-30 | TRUE
Delta Tables 1 | Table 4.2-31. CV/VAV Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) | 31 | CV/VAV Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) | Table 4.2-31. CV/VAV Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) | 4.2-31 | TRUE
Delta Tables 1 | Table 4.2-32. CV/VAV Delta Latent Cooling Coil Load, CV - VAV (kWh/h) | 32 | CV/VAV Delta Latent Cooling Coil Load, CV - VAV (kWh/h) | Table 4.2-32. CV/VAV Delta Latent Cooling Coil Load, CV - VAV (kWh/h) | 4.2-32 | TRUE
Delta Tables 1 | Table 4.2-33. CV/VAV Delta Total Cooling Coil Load, CV - VAV (kWh/h) | 33 | CV/VAV Delta Total Cooling Coil Load, CV - VAV (kWh/h) | Table 4.2-33. CV/VAV Delta Total Cooling Coil Load, CV - VAV (kWh/h) | 4.2-33 | TRUE
Delta Tables 2 | Table 4.2-34. CV Delta Cooling Coil Load, Economizer Operation (kWh/h) | 34 | CV Delta Cooling Coil Load, Economizer Operation (kWh/h) | Table 4.2-34. CV Delta Cooling Coil Load, Economizer Operation (kWh/h) | 4.2-34 | TRUE
Delta Tables 2 | Table 4.2-35. VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) | 35 | VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) | Table 4.2-35. VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) | 4.2-35 | TRUE

## scrape Table names (old) (hidden)
worksheet | Table Name | sequence | Table Name Root | New Table Name | number
Tables 1 | Table 4.2-1. CV/VAV Total Sensible Coil Load (kWh/h) | 1 | CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h) | Table 4.2-1. CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h) | 4.2-1
Tables 1 | Table 4.2-2. CV/VAV Total Sensible and Latent Coil Load (kWh/h) | 2 | CV/VAV Total Coil Load, Heating + Cooling, Sensible and Latent (kWh/h) | Table 4.2-2. CV/VAV Total Coil Load, Heating + Cooling, Sensible and Latent (kWh/h) | 4.2-2
Tables 1 | Table 4.2-3. CV/VAV Pre-Heating Coil Load (kWh/h) | 3 | CV/VAV Pre-Heating Coil Load (kWh/h) | Table 4.2-3. CV/VAV Pre-Heating Coil Load (kWh/h) | 4.2-3
Tables 1 | Table 4.2-4. CV/VAV Total Cooling Coil Load (kWh/h) | 4 | CV/VAV Total Cooling Coil Load (kWh/h) | Table 4.2-4. CV/VAV Total Cooling Coil Load (kWh/h) | 4.2-4
Tables 1 | Table 4.2-5. CV/VAV Sensible Cooling Coil Load (kWh/h) | 5 | CV/VAV Sensible Cooling Coil Load (kWh/h) | Table 4.2-5. CV/VAV Sensible Cooling Coil Load (kWh/h) | 4.2-5
Tables 1 | Table 4.2-6. CV/VAV Latent Cooling Coil Load (kWh/h) | 6 | CV/VAV Latent Cooling Coil Load (kWh/h) | Table 4.2-6. CV/VAV Latent Cooling Coil Load (kWh/h) | 4.2-6
Tables 1 | Table 4.2-7. CV/VAV Cooling Coil Outlet Relative Humidity (%) | 7 | CV/VAV Cooling Coil Outlet Relative Humidity (%) | Table 4.2-7. CV/VAV Cooling Coil Outlet Relative Humidity (%) | 4.2-7
Tables 1 | Table 4.2-8. CV/VAV Zone 1 Reheat Coil Load (kWh/h) | 8 | CV/VAV Zone 1 Reheat Coil Load (kWh/h) | Table 4.2-8. CV/VAV Zone 1 Reheat Coil Load (kWh/h) | 4.2-8
Tables 1 | Table 4.2-9. CV/VAV Zone 2 Reheat Coil Load (kWh/h) | 9 | CV/VAV Zone 2 Reheat Coil Load (kWh/h) | Table 4.2-9. CV/VAV Zone 2 Reheat Coil Load (kWh/h) | 4.2-9
Tables 1 | Table 4.2-10. Outdoor Air Humidity Ratio (g/gda) | 10 | Outdoor Air Humidity Ratio (g/gda) | Table 4.2-10. Outdoor Air Humidity Ratio (g/gda) | 4.2-10
Tables 1 | Table 4.2-11. Outdoor Air Mass Flow Rate (kgda/s) | 11 | Outdoor Air Mass Flow Rate (kgda/s) | Table 4.2-11. Outdoor Air Mass Flow Rate (kgda/s) | 4.2-11
Tables 1 | Table 4.2-12. Cooling Coil Outlet Air Temperature (°C) | 12 | Cooling Coil Outlet Air Temperature (°C) | Table 4.2-12. Cooling Coil Outlet Air Temperature (°C) | 4.2-12
Tables 1 | Table 4.2-13. Supply Air Temperature (°C) | 13 | Supply Air Temperature (°C) | Table 4.2-13. Supply Air Temperature (°C) | 4.2-13
Tables 1 | Table 4.2-14. Supply Air Humidity Ratio (g/gda) | 14 | Supply Air Humidity Ratio (g/gda) | Table 4.2-14. Supply Air Humidity Ratio (g/gda) | 4.2-14
Tables 1 | Table 4.2-15. Supply Air Specific Volume (L/kgda) | 15 | Supply Air Specific Volume (L/kgda) | Table 4.2-15. Supply Air Specific Volume (L/kgda) | 4.2-15
Tables 1 | Table 4.2-16. Supply Air Enthalpy (j/gda) | 16 | Supply Air Enthalpy (j/gda) | Table 4.2-16. Supply Air Enthalpy (j/gda) | 4.2-16
Tables 1 | Table 4.2-17. Supply Air Mass Flow Rate (kgda/s) | 17 | Supply Air Mass Flow Rate (kgda/s) | Table 4.2-17. Supply Air Mass Flow Rate (kgda/s) | 4.2-17
Tables 1 | Table 4.2-18. Zone 1 Supply Air Temperature (°C) | 18 | Zone 1 Supply Air Temperature (°C) | Table 4.2-18. Zone 1 Supply Air Temperature (°C) | 4.2-18
Tables 1 | Table 4.2-19. Zone 1 Air Temperature (°C) | 19 | Zone 1 Air Temperature (°C) | Table 4.2-19. Zone 1 Air Temperature (°C) | 4.2-19
Tables 1 | Table 4.2-20. Zone 1 Humidity Ratio (g/gda) | 20 | Zone 1 Humidity Ratio (g/gda) | Table 4.2-20. Zone 1 Humidity Ratio (g/gda) | 4.2-20
Tables 1 | Table 4.2-21. Zone 2 Air Temperature (°C) | 21 | Zone 2 Air Temperature (°C) | Table 4.2-21. Zone 2 Air Temperature (°C) | 4.2-21
Tables 1 | Table 4.2-22. Zone 2 Supply Air Temperature (°C) | 22 | Zone 2 Supply Air Temperature (°C) | Table 4.2-22. Zone 2 Supply Air Temperature (°C) | 4.2-22
Tables 1 | Table 4.2-23. Zone 2 Humidity Ratio (g/gda) | 23 | Zone 2 Humidity Ratio (g/gda) | Table 4.2-23. Zone 2 Humidity Ratio (g/gda) | 4.2-23
Tables 1 | Table 4.2-24. Supply Fan Air Temperature Rise (°C) | 24 | Supply Fan Air Temperature Rise (°C) | Table 4.2-24. Supply Fan Air Temperature Rise (°C) | 4.2-24
Tables 1 | Table 4.2-25. Return Fan Air Temperature Rise (°C) | 25 | Return Fan Air Temperature Rise (°C) | Table 4.2-25. Return Fan Air Temperature Rise (°C) | 4.2-25
Tables 1 | Table 4.2-26. Zone 1 Humidity Ratio Increase (g/gda) | 26 | Zone 1 Humidity Ratio Increase (g/gda) | Table 4.2-26. Zone 1 Humidity Ratio Increase (g/gda) | 4.2-26
Tables 1 | Table 4.2-27. Zone 2 Humidity Ratio Increase (g/gda) | 27 | Zone 2 Humidity Ratio Increase (g/gda) | Table 4.2-27. Zone 2 Humidity Ratio Increase (g/gda) | 4.2-27
Delta Tables 1 | Table 4.2-28. Delta Preheat Coil Load, CV - VAV (kWh/h) | 28 | Delta Preheat Coil Load, CV - VAV (kWh/h) | Table 4.2-28. Delta Preheat Coil Load, CV - VAV (kWh/h) | 4.2-28
Delta Tables 1 | Table 4.2-29. Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) | 29 | Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) | Table 4.2-29. Delta Sensible Cooling Coil Load, CV - VAV (kWh/h) | 4.2-29
Delta Tables 1 | Table 4.2-30. Delta Latent Cooling Coil Load, CV - VAV (kWh/h) | 30 | Delta Latent Cooling Coil Load, CV - VAV (kWh/h) | Table 4.2-30. Delta Latent Cooling Coil Load, CV - VAV (kWh/h) | 4.2-30
Delta Tables 1 | Table 4.2-31. Delta Total Cooling Coil Load, CV - VAV (kWh/h) | 31 | Delta Total Cooling Coil Load, CV - VAV (kWh/h) | Table 4.2-31. Delta Total Cooling Coil Load, CV - VAV (kWh/h) | 4.2-31
Delta Tables 2 | Table 4.2-32. CV Delta Cooling Coil Load, Economizer - No Economizer Operation (kWh/h) | 32 | CV Delta Cooling Coil Load, Economizer - No Economizer Operation (kWh/h) | Table 4.2-32. CV Delta Cooling Coil Load, Economizer - No Economizer Operation (kWh/h) | 4.2-32
Delta Tables 2 | Table 4.2-33. VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) | 33 | VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) | Table 4.2-33. VAV Delta Cooling Coil Load, Economizer Operation (kWh/h) | 4.2-33

## Tables 1
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.2
Example Results for Section 11, Airside HVAC BESTEST Cases AE301 through AE445
Table B16.7.2-1. CV/VAV Total Coil Load, Heating + Cooling, Sensible & Latent (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 19.0488 | 19.0593 | 19.1295 | 19.8705 | 19.2113 | 19.356 | 19.0403 | 20.0283
AE303 | 11.4511 | 11.4144 | 10.8958 | 10.8891 | 11.0198 | 11.037 | 11.4352 | 11.2303
AE304 | 19.0908 | 19.0527 | 19.2794 | 18.1695 | 19.1753 | 18.996 | 19.0917 | 18.6459
AE305 | 14.1016 | 14.0589 | 13.6189 | 13.2243 | 13.7663 | 13.749 | 14.0864 | 13.6904
AE306 | 19.0892 | 19.0285 | 19.24 | 18.4116 | 19.1067 | 18.957 | 19.0823 | 18.8012
AE326 | 25.4875 | 25.4099 | 25.4312 | 24.358 | 25.395 | 25.208 | 25.5104 | 25.141
AE345 | 14.4191 | 14.391 | 13.9062 | 13.6152 | 14.0581 | 14.083 | 14.429 | 14.0329
AE401 | 19.6363 | 19.6167 | 19.7028 | 20.4162 | 19.7485 | 19.901 | 19.6163
AE403 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476
AE404 | 13.3232 | 13.348 | 14.0307 | 13.3755 | 13.6879 | 13.645 | 13.3076
AE405 | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091
AE406 | 8.2233 | 8.2162 | 8.5955 | 8.1749 | 8.4235 | 8.435 | 8.2187
AE426 | 8.8305 | 8.8241 | 9.2072 | 8.8308 | 8.9313 | 8.972 | 8.8045
AE445 | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448
Table B16.7.2-2. CV/VAV Total Sensible Coil Load, Heating + Cooling (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 19.0488 | 19.0593 | 19.1295 | 19.8705 | 19.2113 | 19.356 | 19.0403 | 20.0283
AE303 | 11.4511 | 11.4144 | 10.8958 | 10.8891 | 11.0198 | 11.037 | 11.4352 | 11.2303
AE304 | 12.8325 | 12.7579 | 12.2686 | 11.9555 | 12.5536 | 12.368 | 12.8301 | 12.0407
AE305 | 14.1016 | 14.0589 | 13.6189 | 13.2243 | 13.7663 | 13.749 | 14.0864 | 13.6904
AE306 | 13.646 | 13.5844 | 13.1365 | 12.9778 | 13.3578 | 13.206 | 13.6388 | 13.0344
AE326 | 13.1857 | 13.0657 | 12.552 | 12.6457 | 12.8634 | 12.65 | 13.2051 | 12.4399
AE345 | 14.4191 | 14.391 | 13.9062 | 13.6152 | 14.0581 | 14.083 | 14.429 | 14.0329
AE401 | 19.6363 | 19.6167 | 19.7028 | 20.4162 | 19.7485 | 19.901 | 19.6163
AE403 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476
AE404 | 7.399 | 7.3735 | 7.4502 | 7.4587 | 7.3706 | 7.333 | 7.3862
AE405 | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091
AE406 | 3.6354 | 3.6094 | 3.6269 | 3.6801 | 3.5834 | 3.567 | 3.6296
AE426 | 3.5938 | 3.5586 | 3.5745 | 3.6423 | 3.5416 | 3.516 | 3.5849
AE445 | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448
Table B16.7.2-3. CV/VAV Pre-Heating Coil Load [QHpreheat] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 2.947 | 2.9697 | 3.58 | 3.7882 | 3.5747 | 3.647 | 2.9467 | 3.7747
AE303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE401 | 10.2597 | 10.2479 | 10.31 | 10.8176 | 10.343 | 10.451 | 10.2578
AE403 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE404 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE405 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE406 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE426 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE445 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table B16.7.2-4. CV/VAV Total Cooling Coil Load [QCtotal] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE303 | 6.7354 | 6.7082 | 6.4595 | 6.4197 | 6.4764 | 6.483 | 6.7255 | 6.5489
AE304 | 16.5785 | 16.5503 | 17.0695 | 16.1037 | 16.778 | 16.662 | 16.5765 | 16.4695
AE305 | 9.3829 | 9.3496 | 9.1806 | 8.9287 | 9.1994 | 9.195 | 9.3734 | 9.1642
AE306 | 14.3643 | 14.3129 | 14.8022 | 14.0314 | 14.4926 | 14.403 | 14.3584 | 14.3284
AE326 | 20.7626 | 20.6943 | 20.9933 | 19.9438 | 20.7797 | 20.654 | 20.7757 | 20.6966
AE345 | 9.7029 | 9.6843 | 9.4684 | 9.2851 | 9.5096 | 9.529 | 9.7073 | 9.5012
AE401 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE403 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476
AE404 | 13.3232 | 13.348 | 14.0307 | 13.3755 | 13.6879 | 13.645 | 13.3076
AE405 | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091
AE406 | 8.2233 | 8.2162 | 8.5955 | 8.1749 | 8.4235 | 8.435 | 8.2187
AE426 | 8.8305 | 8.8241 | 9.2072 | 8.8308 | 8.9313 | 8.972 | 8.8045
AE445 | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448
Table B16.7.2-5. CV/VAV Sensible Cooling Coil Load [QCsensible] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE303 | 6.7354 | 6.7082 | 6.4595 | 6.4197 | 6.4764 | 6.483 | 6.7255 | 6.5489
AE304 | 10.3202 | 10.2556 | 10.0587 | 9.8897 | 10.1563 | 10.034 | 10.315 | 9.8644
AE305 | 9.3829 | 9.3496 | 9.1806 | 8.9287 | 9.1994 | 9.195 | 9.3734 | 9.1642
AE306 | 8.9211 | 8.8688 | 8.6987 | 8.5975 | 8.7437 | 8.652 | 8.9149 | 8.5615
AE326 | 8.4609 | 8.3501 | 8.1141 | 8.2315 | 8.2481 | 8.096 | 8.4705 | 7.9955
AE345 | 9.7029 | 9.6843 | 9.4684 | 9.2851 | 9.5096 | 9.529 | 9.7073 | 9.5012
AE401 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE403 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476
AE404 | 7.399 | 7.3735 | 7.4502 | 7.4587 | 7.3706 | 7.333 | 7.3862
AE405 | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091
AE406 | 3.6354 | 3.6094 | 3.6269 | 3.6801 | 3.5834 | 3.567 | 3.6296
AE426 | 3.5938 | 3.5586 | 3.5745 | 3.6423 | 3.5416 | 3.516 | 3.5849
AE445 | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448
Table B16.7.2-6. CV/VAV Latent Cooling Coil Load [QClatent] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE304 | 6.2583 | 6.2947 | 7.0108 | 6.214 | 6.6217 | 6.629 | 6.2615 | 6.6051
AE305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE306 | 5.4432 | 5.4441 | 6.1035 | 5.4338 | 5.7489 | 5.75 | 5.4435 | 5.7668
AE326 | 12.3018 | 12.3442 | 12.8792 | 11.7123 | 12.5316 | 12.558 | 12.3053 | 12.7011
AE345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE401 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE403 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE404 | 5.9242 | 5.9745 | 6.5805 | 5.9168 | 6.3173 | 6.313 | 5.9214
AE405 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE406 | 4.5879 | 4.6068 | 4.9686 | 4.4948 | 4.84 | 4.868 | 4.5892
AE426 | 5.2366 | 5.2655 | 5.6327 | 5.1885 | 5.3897 | 5.456 | 5.2196
AE445 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table B16.7.2-7. CV/VAV Zone 1 Reheat Coil Load [QH1reheat] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 7.7129 | 7.7075 | 7.4721 | 7.706 | 7.5057 | 7.539 | 7.7093 | 7.7894
AE303 | 2.2584 | 2.2547 | 2.1363 | 2.15 | 2.1827 | 2.188 | 2.2552 | 2.245
AE304 | 0.99332 | 0.98884 | 0.85904 | 0.79774 | 0.94208 | 0.915 | 0.99153 | 0.84482
AE305 | 2.2598 | 2.2561 | 2.1367 | 2.0723 | 2.193 | 2.188 | 2.2567 | 2.1752
AE306 | 2.2625 | 2.2588 | 2.1374 | 2.1107 | 2.2136 | 2.188 | 2.2618 | 2.1522
AE326 | 2.2625 | 2.2588 | 2.1374 | 2.1256 | 2.2141 | 2.188 | 2.2668 | 2.1398
AE345 | 2.2587 | 2.255 | 2.1374 | 2.0887 | 2.1849 | 2.188 | 2.2607 | 2.1776
AE401 | 4.4994 | 4.4963 | 4.5019 | 4.5839 | 4.5034 | 4.524 | 4.4895
AE403 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE404 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE405 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE406 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE426 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE445 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table B16.7.2-8. CV/VAV Zone 2 Reheat Coil Load [QH2reheat] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 8.3889 | 8.3822 | 8.0774 | 8.3763 | 8.1309 | 8.17 | 8.3843 | 8.4642
AE303 | 2.4572 | 2.4515 | 2.3 | 2.3194 | 2.3607 | 2.366 | 2.4545 | 2.4364
AE304 | 1.519 | 1.5135 | 1.3509 | 1.2681 | 1.4552 | 1.419 | 1.5236 | 1.3315
AE305 | 2.4589 | 2.4532 | 2.3017 | 2.2232 | 2.3739 | 2.366 | 2.4562 | 2.351
AE306 | 2.4624 | 2.4568 | 2.3004 | 2.2695 | 2.4005 | 2.366 | 2.4621 | 2.3206
AE326 | 2.4624 | 2.4568 | 2.3005 | 2.2886 | 2.4012 | 2.366 | 2.4678 | 2.3046
AE345 | 2.4575 | 2.4518 | 2.3005 | 2.2414 | 2.3635 | 2.366 | 2.461 | 2.3541
AE401 | 4.8772 | 4.8725 | 4.891 | 5.0147 | 4.9022 | 4.926 | 4.8689
AE403 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE404 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE405 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE406 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE426 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE445 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table B16.7.2-9. CV/VAV Outdoor Air Temperature (°F)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29
AE303 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
AE304 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9
AE305 | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9
AE306 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AE326 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AE345 | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9
AE401 | -29 | -29 | -29 | -29 | -29 | -29 | -29
AE403 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
AE404 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9
AE405 | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9
AE406 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AE426 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AE445 | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9
Table B16.7.2-10. CV/VAV Outdoor Air Humidity Ratio (g/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | 0.00025893
AE303 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029359 | 0.0029317
AE304 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016774 | 0.016766
AE305 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.0044783
AE306 | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.01556
AE326 | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.01556
AE345 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.0044783
AE401 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893
AE403 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029359
AE404 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016774
AE405 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909
AE406 | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556
AE426 | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556
AE445 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909
Table B16.7.2-11. CV/VAV Outdoor Air Mass Flow Rate (kgda/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0.28139 | 0.28143 | 0.28316 | 0.29649 | 0.28418 | 0.28316 | 0.2814 | 0.29647
AE303 | 0.27809 | 0.27814 | 0.28316 | 0.28151 | 0.28418 | 0.28316 | 0.27808 | 0.28996
AE304 | 0.27554 | 0.27557 | 0.28316 | 0.2735 | 0.28418 | 0.28316 | 0.27553 | 0.28179
AE305 | 0.2774 | 0.27745 | 0.28316 | 0.27741 | 0.28418 | 0.28316 | 0.27739 | 0.28575
AE306 | 0.27605 | 0.27609 | 0.28316 | 0.27538 | 0.28418 | 0.28316 | 0.27604 | 0.28374
AE326 | 0.74832 | 0.74842 | 0.73624 | 0.71372 | 0.73888 | 0.73624 | 0.74833 | 0.73521
AE345 | 0.75353 | 0.75367 | 0.73624 | 0.72169 | 0.73888 | 0.73624 | 0.75354 | 0.74345
AE401 | 0.28139 | 0.28143 | 0.28316 | 0.29707 | 0.28418 | 0.28316 | 0.2814
AE403 | 0.27809 | 0.27814 | 0.28316 | 0.28597 | 0.28418 | 0.28316 | 0.27808
AE404 | 0.27533 | 0.27537 | 0.28316 | 0.27289 | 0.28418 | 0.28316 | 0.27532
AE405 | 0.2774 | 0.27745 | 0.28316 | 0.27761 | 0.28418 | 0.28316 | 0.27739
AE406 | 0.27552 | 0.27556 | 0.28316 | 0.27474 | 0.28418 | 0.28316 | 0.27552
AE426 | 0.33213 | 0.33253 | 0.33835 | 0.32941 | 0.33144 | 0.33354 | 0.33133
AE445 | 0.33495 | 0.33538 | 0.33832 | 0.33586 | 0.33427 | 0.33354 | 0.33411
Table B16.7.2-12. CV/VAV Cooling Coil Outlet Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 7.2222 | 7.2222 | 7.22 | 7.2222 | 7.22 | 7.22 | 7.22 | 7.2206
AE303 | 12.2066 | 12.2059 | 12.2049 | 12.1667 | 12.197 | 12.199 | 12.215 | 12.2045
AE304 | 12.2072 | 12.2065 | 12.2047 | 12.2222 | 12.2012 | 12.199 | 12.2114 | 12.1878
AE305 | 12.2068 | 12.2061 | 12.2049 | 12.2778 | 12.1989 | 12.199 | 12.2132 | 12.196
AE306 | 12.2072 | 12.2065 | 12.1759 | 12.2222 | 12.2019 | 12.199 | 12.2138 | 12.1919
AE326 | 12.2072 | 12.2065 | 12.2038 | 12.2222 | 12.2017 | 12.199 | 12.2 | 12.1899
AE345 | 12.2066 | 12.2059 | 12.2049 | 12.2222 | 12.197 | 12.199 | 12.2 | 12.1964
AE401 | 7.2222 | 7.2222 | 7.22 | 7.2222 | 7.2031 | 7.22 | 7.22
AE403 | 12.6643 | 12.6466 | 12.6699 | 12.6667 | 12.6598 | 12.66 | 12.6692
AE404 | 12.4805 | 12.4612 | 12.4633 | 12.4444 | 12.4725 | 12.47 | 12.491
AE405 | 12.6644 | 12.6468 | 12.6704 | 12.6667 | 12.661 | 12.66 | 12.6697
AE406 | 12.6647 | 12.6472 | 12.6693 | 12.6667 | 12.6637 | 12.66 | 12.6584
AE426 | 12.6647 | 12.6472 | 12.6574 | 12.6667 | 12.6638 | 12.66 | 12.67
AE445 | 12.6644 | 12.6519 | 12.6704 | 12.6667 | 12.6608 | 12.66 | 12.67
Table B16.7.2-13. CV/VAV Cooling Coil Outlet Relative Humidity [RHcco] (%)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 24.7331 | 24.7328 |  | 23.9613 | 23.8906 | 24.65 | 24.6351 | 22.4118
AE303 | 48.1495 | 47.6873 | 48.22 | 47.9247 | 47.4569 | 48.02 | 48.1783 | 49.1748
AE304 | 100 | 99.9992 | 95.49 | 100 | 99.1258 | 100 | 100 | 98.0574
AE305 | 65.719 | 65.3364 | 65.84 | 65.5319 | 64.909 | 65.57 | 65.7465 | 66.2464
AE306 | 100 | 99.9992 | 96.21 | 100 | 99.2475 | 100 | 100 | 98.3662
AE326 | 100 | 99.9992 | 98.89 | 100 | 99.9275 | 100 | 100 | 97.9418
AE345 | 51.0891 | 50.7067 | 51.33 | 51.1359 | 50.9944 | 51.1 | 51.1113 | 51.0089
AE401 | 4.1447 | 4.1474 |  | 4.8015 | 4.1501 | 4.17 | 4.1464
AE403 | 36.3949 | 36.0086 | 36.39 | 34.2896 | 35.8492 | 35.98 | 36.3722
AE404 | 100 | 99.9992 | 97.24 | 100 | 98.7059 | 100 | 100
AE405 | 53.4629 | 53.1717 | 53.52 | 51.8548 | 52.7786 | 53.05 | 53.4325
AE406 | 100 | 99.9992 | 99.38 | 100 | 99.7649 | 100 | 100
AE426 | 100 | 99.9992 | 99.58 | 100 | 99.9528 | 100 | 100
AE445 | 49.575 | 49.2421 | 49.78 | 49.664 | 49.4632 | 49.58 | 49.5567
Table B16.7.2-14. CV/VAV Supply Fan Air Temperature Rise (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0.5616 | 0.56226 | 0.5899 | 0.55556 | 0.58627 | 0.5818 | 0.56149 | 0.56288
AE303 | 0.57122 | 0.57189 | 0.5899 | 0.61111 | 0.58339 | 0.5818 | 0.57113 | 0.5755
AE304 | 0.5706 | 0.57126 | 0.5899 | 0.61111 | 0.5785 | 0.5818 | 0.5705 | 0.59219
AE305 | 0.57101 | 0.57168 | 0.5899 | 0.61111 | 0.58174 | 0.5818 | 0.57091 | 0.58399
AE306 | 0.5706 | 0.57126 | 0.5899 | 0.55556 | 0.57849 | 0.5818 | 0.5705 | 0.58812
AE326 | 0.5706 | 0.57126 | 0.5899 | 0.55556 | 0.57843 | 0.5818 | 0.57048 | 0.59014
AE345 | 0.57119 | 0.57185 | 0.5899 | 0.55556 | 0.58306 | 0.5818 | 0.57106
AE401 | 0.074611 | 0.086087 | 0.087254 | 0.055556 | 0.086922 | 0.0903 | 0.074852
AE403 | 0.1135 | 0.13116 | 0.1251 | 0.11111 | 0.1202 | 0.1195 | 0.11296
AE404 | 0.29723 | 0.31661 | 0.32831 | 0.33333 | 0.30715 | 0.3146 | 0.29011
AE405 | 0.11338 | 0.13101 | 0.12457 | 0.11111 | 0.11918 | 0.1195 | 0.11281
AE406 | 0.11304 | 0.1306 | 0.12459 | 0.11111 | 0.11634 | 0.1195 | 0.11249
AE426 | 0.11304 | 0.1306 | 0.12459 | 0.11111 | 0.11633 | 0.1195 | 0.11216
AE445 | 0.1134 | 0.12586 | 0.12457 | 0.11111 | 0.11933 | 0.1195 | 0.11252
Table B16.7.2-15. CV/VAV Supply Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 7.7838 | 7.7845 | 7.8099 | 7.7778 | 7.8063 | 7.8018 | 7.7815 | 7.7835
AE303 | 12.7778 | 12.7778 | 12.7948 | 12.7778 | 12.7804 | 12.7808 | 12.7861 | 12.78
AE304 | 12.7778 | 12.7778 | 12.7946 | 12.8333 | 12.7797 | 12.7808 | 12.7819 | 12.78
AE305 | 12.7778 | 12.7778 | 12.7948 | 12.8889 | 12.7806 | 12.7808 | 12.7841 | 12.78
AE306 | 12.7778 | 12.7778 | 12.7658 | 12.7778 | 12.7804 | 12.7808 | 12.7843 | 12.78
AE326 | 12.7778 | 12.7778 | 12.7937 | 12.7778 | 12.7801 | 12.7808 | 12.7705 | 12.78
AE345 | 12.7778 | 12.7778 | 12.7948 | 12.7778 | 12.78 | 12.7808 | 12.7711 | 12.78
AE401 | 7.2968 | 7.3083 | 7.3073 | 7.2778 | 7.2901 | 7.3103 | 7.2949
AE403 | 12.7778 | 12.7778 | 12.795 | 12.7778 | 12.78 | 12.7795 | 12.7822
AE404 | 12.7778 | 12.7778 | 12.7916 | 12.7778 | 12.7797 | 12.7846 | 12.7811
AE405 | 12.7778 | 12.7778 | 12.795 | 12.7778 | 12.7802 | 12.7795 | 12.7825
AE406 | 12.7778 | 12.7778 | 12.7939 | 12.7778 | 12.78 | 12.7795 | 12.7709
AE426 | 12.7778 | 12.7778 | 12.782 | 12.7778 | 12.7801 | 12.7795 | 12.7822
AE445 | 12.7778 | 12.7778 | 12.795 | 12.7778 | 12.7802 | 12.7795 | 12.7825
Table B16.7.2-16. CV/VAV Supply Air Humidity Ratio (g/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0.0015483 | 0.0015484 | 0.0015343 | 0.0015 | 0.0014957 | 0.001549 | 0.0015419 | 0.0014025
AE303 | 0.0042307 | 0.0041899 | 0.0042354 | 0.0042 | 0.0041681 | 0.004234 | 0.0042356 | 0.0043208
AE304 | 0.0088518 | 0.008852 | 0.0084426 | 0.0089 | 0.0087725 | 0.008891 | 0.0088543 | 0.0086662
AE305 | 0.0057889 | 0.0057551 | 0.0057974 | 0.0058 | 0.0057157 | 0.005795 | 0.0057938 | 0.0058316
AE306 | 0.0088518 | 0.008852 | 0.0084916 | 0.0089 | 0.0087839 | 0.008888 | 0.0088557 | 0.0086963
AE326 | 0.0088518 | 0.008852 | 0.0087474 | 0.0089 | 0.0088448 | 0.008909 | 0.0088476 | 0.0086571
AE345 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.0044807
AE401 | 0.00025893 | 0.00025861 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893
AE403 | 0.0032906 | 0.0032519 | 0.0032876 | 0.0031 | 0.003241 | 0.003265 | 0.0032889
AE404 | 0.0090147 | 0.0090036 | 0.0087492 | 0.009 | 0.0088944 | 0.009056 | 0.009017
AE405 | 0.0048458 | 0.004814 | 0.004851 | 0.0047 | 0.0047837 | 0.004826 | 0.004835
AE406 | 0.009126 | 0.0091159 | 0.0090684 | 0.0092 | 0.0091064 | 0.009175 | 0.0091221
AE426 | 0.009126 | 0.0091159 | 0.0090802 | 0.0092 | 0.0091238 | 0.009184 | 0.0091292
AE445 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909
Table B16.7.2-17. CV/VAV Supply Air Specific Volume (L/kgda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 797.8282 | 797.7263 | 833.33 |  | 830.3519 |  | 793.9174 | 797.6468
AE303 | 815.504 | 815.3446 | 833.33 |  | 830.3519 |  | 811.5517 | 815.634
AE304 | 821.5223 | 821.4151 | 833.33 |  | 830.3519 |  | 817.5256 | 821.2933
AE305 | 817.5333 | 817.3825 | 833.33 |  | 830.3519 |  | 813.5654 | 817.6016
AE306 | 821.5223 | 821.4151 | 833.33 |  | 830.3519 |  | 817.5341 | 821.3324
AE326 | 821.5223 | 821.4151 | 833.33 |  | 830.3519 |  | 817.4842 | 821.2814
AE345 | 815.8428 | 815.6925 | 833.33 |  | 830.3519 |  | 811.8397 | 815.8422
AE401 | 794.7981 | 794.7275 | 833.33 |  | 830.3519 |  | 794.2783
AE403 | 814.2796 | 814.1232 | 833.33 |  | 830.3519 |  | 813.5066
AE404 | 821.7345 | 821.6126 | 833.33 |  | 830.3519 |  | 819.6593
AE405 | 816.3051 | 816.1571 | 833.33 |  | 830.3519 |  | 815.5201
AE406 | 821.8794 | 821.7587 | 833.33 |  | 830.3519 |  | 821.0663
AE426 | 821.8794 | 821.7587 | 833.33 |  | 830.3519 |  | 821.1102
AE445 | 815.8428 | 815.6925 | 833.33 |  | 830.3519 |  | 815.0746
Table B16.7.2-18. CV/VAV Supply Air Enthalpy (J/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 11.726 |  | 11.71 |  | 11.6064 |  | 11.7069 | 11.3582
AE303 | 23.5371 |  | 23.55 |  | 23.3653 |  | 23.5569 | 23.7658
AE304 | 35.2043 |  | 34.16 |  | 34.9895 |  | 35.2138 | 34.737
AE305 | 27.4712 |  | 27.49 |  | 27.2729 |  | 27.489 | 27.5803
AE306 | 35.2043 |  | 34.26 |  | 35.0189 |  | 35.2197 | 34.8128
AE326 | 35.2043 |  | 34.93 |  | 35.1723 |  | 35.185 | 34.7138
AE345 | 24.194 |  | 24.24 |  | 24.155 |  | 24.186 | 24.1695
AE401 | 7.9923 |  | 8 |  | 7.9766 |  | 7.9897
AE403 | 21.1635 |  | 21.16 |  | 21.0244 |  | 21.1625
AE404 | 35.6156 |  | 34.93 |  | 35.2972 |  | 35.6235
AE405 | 25.0901 |  | 25.1 |  | 24.9195 |  | 25.0664
AE406 | 35.8965 |  | 35.74 |  | 35.8327 |  | 35.8787
AE426 | 35.8965 |  | 35.76 |  | 35.8769 |  | 35.908
AE445 | 24.194 |  | 24.24 |  | 24.1552 |  | 24.1977
Table B16.7.2-19. CV/VAV Supply Air Mass Flow Rate (kgda/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0.77054 | 0.77064 | 0.73624 | 0.77088 | 0.73888 | 0.73624 | 0.77055 | 0.77082
AE303 | 0.75384 | 0.75399 | 0.73624 | 0.73193 | 0.73888 | 0.73624 | 0.7538 | 0.75391
AE304 | 0.74832 | 0.74842 | 0.73624 | 0.71109 | 0.73888 | 0.73624 | 0.74829 | 0.73267
AE305 | 0.75197 | 0.75211 | 0.73624 | 0.72126 | 0.73888 | 0.73624 | 0.75194 | 0.74296
AE306 | 0.74832 | 0.74842 | 0.73624 | 0.716 | 0.73888 | 0.73624 | 0.74829 | 0.73774
AE326 | 0.74832 | 0.74842 | 0.73624 | 0.71372 | 0.73888 | 0.73624 | 0.74833 | 0.73521
AE345 | 0.75353 | 0.75367 | 0.73624 | 0.72169 | 0.73888 | 0.73624 | 0.75354 | 0.74345
AE401 | 0.28139 | 0.28143 | 0.28316 | 0.29707 | 0.28418 | 0.28316 | 0.2814
AE403 | 0.33569 | 0.33612 | 0.3385 | 0.33688 | 0.3351 | 0.33354 | 0.33495
AE404 | 0.53919 | 0.53988 | 0.54925 | 0.53541 | 0.53845 | 0.54137 | 0.53882
AE405 | 0.33473 | 0.33516 | 0.33832 | 0.33591 | 0.33415 | 0.33354 | 0.33393
AE406 | 0.33213 | 0.33253 | 0.33835 | 0.32968 | 0.33145 | 0.33354 | 0.33137
AE426 | 0.33213 | 0.33253 | 0.33835 | 0.32941 | 0.33144 | 0.33354 | 0.33133
AE445 | 0.33495 | 0.33538 | 0.33832 | 0.33586 | 0.33427 | 0.33354 | 0.33411
Table B16.7.2-20. CV/VAV Outdoor Air Mass Flow to Supply Air Mass Flow Ratio (fraction)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0.36519 | 0.36519 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36519 | 0.38461
AE303 | 0.3689 | 0.36889 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36891 | 0.38461
AE304 | 0.36821 | 0.36821 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36821 | 0.38461
AE305 | 0.3689 | 0.36889 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36891 | 0.38461
AE306 | 0.3689 | 0.3689 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.3689 | 0.38461
AE326 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
AE345 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
AE401 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99999
AE403 | 0.82841 | 0.82752 | 0.83653 | 0.8489 | 0.84805 | 0.84895 | 0.83021
AE404 | 0.51064 | 0.51006 | 0.51555 | 0.50968 | 0.52778 | 0.52304 | 0.51097
AE405 | 0.82871 | 0.82782 | 0.83698 | 0.82645 | 0.85046 | 0.84895 | 0.83068
AE406 | 0.82954 | 0.82866 | 0.83688 | 0.83333 | 0.85738 | 0.84895 | 0.83144
AE426 | 1 | 1 | 1 | 1 | 1 | 1 | 1
AE445 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Table B16.7.2-21. CV/VAV Zone 1 Supply Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 29.2787 | 29.2883 | 29.6699 |  | 29.649 | 29.5754 | 29.27 | 29.5476
AE303 | 19.1796 | 19.1761 | 19.05 |  | 19.1013 | 19.1006 | 19.18 | 19.1935
AE304 | 15.5904 | 15.5808 | 15.3101 |  | 15.485 | 15.4247 | 15.59 | 15.2634
AE305 | 19.1811 | 19.1778 | 19.0515 |  | 19.1133 | 19.1006 | 19.18 | 19.0856
AE306 | 19.1841 | 19.1807 | 19.0246 |  | 19.1369 | 19.1006 | 19.19 | 19.0631
AE326 | 19.1841 | 19.1807 | 19.0525 |  | 19.1373 | 19.1006 | 19.19 | 19.0484
AE345 | 19.1799 | 19.1765 | 19.0515 |  | 19.1037 | 19.1006 | 19.18 | 19.0884
AE401 | 46.92 | 46.9483 | 46.8548 |  | 46.6969 | 46.5047 | 46.8281
AE403 | 12.7778 | 12.7777 | 12.795 |  | 12.78 | 12.7795 | 12.7822
AE404 | 12.7778 | 12.7777 | 12.7916 |  | 12.7808 | 12.7846 | 12.7878
AE405 | 12.7778 | 12.7777 | 12.795 |  | 12.7802 | 12.7795 | 12.7825
AE406 | 12.7778 | 12.7777 | 12.7939 |  | 12.7899 | 12.7795 | 12.7709
AE426 | 12.7778 | 12.7777 | 12.782 |  | 12.79 | 12.7795 | 12.7822
AE445 | 12.7778 | 12.7778 | 12.795 |  | 12.7802 | 12.7795 | 12.7825
Table B16.7.2-22. CV/VAV Zone 1 Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 21.1111 | 21.1111 | 21.111 | 21.1111 | 21.1299 | 21.1106 | 21.1102 | 21.111
AE303 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3285 | 23.333
AE304 | 23.8889 | 23.8889 | 23.889 | 23.8889 | 23.8914 | 23.8893 | 23.8806 | 23.889
AE305 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3269 | 23.333
AE306 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3339 | 23.333
AE326 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3337 | 23.333
AE345 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.328 | 23.333
AE401 | 21.1111 | 21.1111 | 21.111 | 21.1111 | 21.1452 | 21.1103 | 21.1151
AE403 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3302
AE404 | 23.8889 | 23.8889 | 23.889 | 23.8889 | 23.9001 | 23.8934 | 23.8829
AE405 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3319
AE406 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.318
AE426 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3286
AE445 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3321
Table B16.7.2-23. CV/VAV Zone 1 Humidity Ratio (g/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0.0021971 | 0.0021972 | 0.0022251 |  | 0.0021723 | 0.002253 | 0.0021868 | 0.0020231
AE303 | 0.0048927 | 0.0048518 | 0.0049298 |  | 0.0048436 | 0.004938 | 0.0048998 | 0.0050918
AE304 | 0.0095185 | 0.0095186 | 0.00914 |  | 0.0094477 | 0.009595 | 0.0095252 | 0.0093595
AE305 | 0.0064526 | 0.0064187 | 0.0064918 |  | 0.0063912 | 0.006499 | 0.0064597 | 0.0065783
AE306 | 0.0095187 | 0.0095189 | 0.00919 |  | 0.0094593 | 0.009592 | 0.0095248 | 0.0093843
AE326 | 0.0095187 | 0.0095189 | 0.0094417 |  | 0.0095202 | 0.009613 | 0.0095166 | 0.0093477
AE345 | 0.0051532 | 0.0051194 | 0.0052044 |  | 0.0051565 | 0.005212 | 0.0051553 | 0.0051637
AE401 | 0.002304 | 0.0023034 | 0.0023324 |  | 0.0022887 | 0.002374 | 0.0022691
AE403 | 0.0049701 | 0.00493 | 0.0049958 |  | 0.0049254 | 0.005021 | 0.0049882
AE404 | 0.0099076 | 0.0098953 | 0.0096515 |  | 0.009788 | 0.00998 | 0.0099213
AE405 | 0.0065301 | 0.006497 | 0.0065572 |  | 0.0064728 | 0.006582 | 0.0065372
AE406 | 0.010823 | 0.010812 | 0.010775 |  | 0.010803 | 0.010931 | 0.010838
AE426 | 0.010823 | 0.010812 | 0.010787 |  | 0.010825 | 0.01094 | 0.010844
AE445 | 0.0061741 | 0.0061387 | 0.0062162 |  | 0.0061691 | 0.006264 | 0.0061921
Table B16.7.2-24. CV/VAV Zone 2 Supply Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 27.8228 | 27.8298 | 28.084 |  | 28.0886 | 28.026 | 27.81 | 28.0547
AE303 | 18.7479 | 18.7408 | 18.57 |  | 18.6401 | 18.637 | 18.75 | 18.7458
AE304 | 16.4644 | 16.4551 | 16.1852 |  | 16.3615 | 16.2939 | 16.48 | 16.135
AE305 | 18.75 | 18.7428 | 18.572 |  | 18.6566 | 18.6371 | 18.75 | 18.6216
AE306 | 18.7541 | 18.747 | 18.5398 |  | 18.6889 | 18.6371 | 18.76 | 18.5869
AE326 | 18.7541 | 18.747 | 18.5677 |  | 18.6896 | 18.637 | 18.76 | 18.5668
AE345 | 18.7483 | 18.7411 | 18.572 |  | 18.6434 | 18.6371 | 18.75 | 18.6255
AE401 | 36.0391 | 36.0548 | 35.9521 |  | 35.8886 | 35.7662 | 35.9884
AE403 | 12.7778 | 12.7777 | 12.795 |  | 12.78 | 12.7795 | 12.7822
AE404 | 12.7778 | 12.7777 | 12.7916 |  | 12.7808 | 12.7846 | 12.7878
AE405 | 12.7778 | 12.7777 | 12.795 |  | 12.7802 | 12.7795 | 12.7825
AE406 | 12.7778 | 12.7777 | 12.7939 |  | 12.7899 | 12.7795 | 12.7709
AE426 | 12.7778 | 12.7777 | 12.782 |  | 12.79 | 12.7795 | 12.7822
AE445 | 12.7778 | 12.7778 | 12.795 |  | 12.7802 | 12.7795 | 12.7825
Table B16.7.2-25. CV/VAV Zone 2 Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 22.2222 | 22.2222 | 22.222 | 22.2222 | 22.2485 | 22.221 | 22.2171 | 22.222
AE303 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.442 | 24.4389 | 24.444
AE304 | 25 | 25 | 25 | 25 | 25.0047 | 25.001 | 25.0027 | 25
AE305 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.4419 | 24.4367 | 24.444
AE306 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.4419 | 24.4427 | 24.444
AE326 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.442 | 24.4424 | 24.444
AE345 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.4419 | 24.4382 | 24.444
AE401 | 22.2222 | 22.2222 | 22.222 | 22.2222 | 22.2593 | 22.2208 | 22.2211
AE403 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4608 | 24.4431 | 24.4386
AE404 | 25 | 25 | 25 | 25 | 25.0168 | 25.0043 | 24.9989
AE405 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4431 | 24.4401
AE406 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4432 | 24.431
AE426 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4431 | 24.4416
AE445 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4431 | 24.442
Table B16.7.2-26. CV/VAV Zone 2 Humidity Ratio (g/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0.0023817 | 0.0023819 | 0.0024213 |  | 0.0023649 | 0.002454 | 0.0023719 | 0.0022113
AE303 | 0.0050812 | 0.0050403 | 0.0051345 |  | 0.0050359 | 0.005139 | 0.0050898 | 0.0052843
AE304 | 0.0097082 | 0.0097084 | 0.00934 |  | 0.00964 | 0.009796 | 0.0097162 | 0.0095576
AE305 | 0.0066415 | 0.0066076 | 0.0066965 |  | 0.0065835 | 0.0067 | 0.0066501 | 0.0067736
AE306 | 0.0097086 | 0.0097087 | 0.00939 |  | 0.0096517 | 0.009793 | 0.0097161 | 0.009581
AE326 | 0.0097086 | 0.0097087 | 0.00965 |  | 0.0097126 | 0.009814 | 0.009708 | 0.0095451
AE345 | 0.0053417 | 0.0053078 | 0.0054091 |  | 0.0053488 | 0.005413 | 0.0053453 | 0.0053589
AE401 | 0.0023101 | 0.0023096 | 0.0023296 |  | 0.0022872 | 0.002374 | 0.0022892
AE403 | 0.0050294 | 0.0049886 | 0.0050706 |  | 0.0049851 | 0.005084 | 0.0050489
AE404 | 0.010241 | 0.010229 | 0.0099979 |  | 0.010124 | 0.010327 | 0.010261
AE405 | 0.0065896 | 0.0065555 | 0.006633 |  | 0.0065327 | 0.006645 | 0.006598
AE406 | 0.010883 | 0.010871 | 0.010849 |  | 0.010863 | 0.010994 | 0.0109
AE426 | 0.010883 | 0.010871 | 0.010861 |  | 0.010885 | 0.011003 | 0.010906
AE445 | 0.0062336 | 0.0061973 | 0.006292 |  | 0.006229 | 0.006327 | 0.006253
Table B16.7.2-27. CV/VAV Moisture Added to Zone 1 by Latent Gains (g/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0.23072 | 0.23076 | 0.23474 |  | 0.23073 | 0.23922 | 0.22932 | 0.22077
AE303 | 0.23034 | 0.23034 | 0.23595 |  | 0.23036 | 0.23922 | 0.23106 | 0.26827
AE304 | 0.23025 | 0.23026 | 0.23699 |  | 0.23026 | 0.23922 | 0.23168 | 0.23444
AE305 | 0.23034 | 0.23035 | 0.23595 |  | 0.23036 | 0.23922 | 0.23106 | 0.25602
AE306 | 0.23034 | 0.23035 | 0.23732 |  | 0.23036 | 0.23922 | 0.23106 | 0.23426
AE326 | 0.23034 | 0.23035 | 0.23595 |  | 0.23036 | 0.23922 | 0.23106 | 0.23434
AE345 | 0.23034 | 0.23035 | 0.23595 |  | 0.23036 | 0.23922 | 0.23106 | 0.23434
AE401 | 0.23072 | 0.23071 | 0.23474 |  | 0.23073 | 0.23923 | 0.22628
AE403 | 0.23034 | 0.23038 | 0.23627 |  | 0.23035 | 0.23924 | 0.23249
AE404 | 0.23025 | 0.23022 | 0.23715 |  | 0.23026 | 0.23924 | 0.23217
AE405 | 0.23034 | 0.23035 | 0.23595 |  | 0.23035 | 0.23924 | 0.23217
AE406 | 0.23034 | 0.23034 | 0.23595 |  | 0.23035 | 0.23924 | 0.23235
AE426 | 0.23034 | 0.23034 | 0.23595 |  | 0.23035 | 0.23924 | 0.23216
AE445 | 0.23034 | 0.23035 | 0.23583 |  | 0.23035 | 0.23924 | 0.23216
[(Zone Supply Air Mass Flow) × {(Zone Humidity Ratio) – (Zone Supply Air Humidity Ratio )} × 1000 g/kg]
Table B16.7.2-28. CV/VAV Moisture Added to Zone 2 by Latent Gains (g/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0.34579 | 0.34587 | 0.35162 |  | 0.34583 | 0.35877 | 0.34437 | 0.33571
AE303 | 0.34523 | 0.34524 | 0.35644 |  | 0.34527 | 0.35877 | 0.34672 | 0.39114
AE304 | 0.34509 | 0.34513 | 0.35577 |  | 0.34513 | 0.35877 | 0.34731 | 0.35166
AE305 | 0.34523 | 0.34522 | 0.35644 |  | 0.34527 | 0.35877 | 0.34672 | 0.37684
AE306 | 0.34523 | 0.34527 | 0.35616 |  | 0.34527 | 0.35877 | 0.34672 | 0.35144
AE326 | 0.34523 | 0.34527 | 0.35784 |  | 0.34527 | 0.35877 | 0.34672 | 0.35154
AE345 | 0.34523 | 0.34522 | 0.35644 |  | 0.34527 | 0.35877 | 0.34672 | 0.35154
AE401 | 0.34579 | 0.3458 | 0.35162 |  | 0.34583 | 0.35883 | 0.34226
AE403 | 0.34523 | 0.3453 | 0.35691 |  | 0.34527 | 0.35889 | 0.34873
AE404 | 0.34509 | 0.34509 | 0.35765 |  | 0.34513 | 0.35899 | 0.34827
AE405 | 0.34523 | 0.34522 | 0.35644 |  | 0.34527 | 0.35889 | 0.34827
AE406 | 0.34523 | 0.34525 | 0.35644 |  | 0.34527 | 0.35889 | 0.34853
AE426 | 0.34523 | 0.34525 | 0.35644 |  | 0.34527 | 0.35889 | 0.34827
AE445 | 0.34523 | 0.34522 | 0.35663 |  | 0.34527 | 0.35889 | 0.34827
[(Zone Supply Air Mass Flow) × {(Zone Humidity Ratio) – (Zone Supply Air Humidity Ratio )} × 1000 g/kg]
Table B16.7.2-29. CV/VAV Return Fan Air Temperature Rise (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 | 0.34819 | 0.29556 | 0.29495 |  | 0.29272 | 0.2909 | 0.34804 | 0.2814
AE303 | 0.33958 | 0.2976 | 0.29495 |  | 0.29128 | 0.2909 | 0.3394 | 0.28773
AE304 | 0.34187 | 0.29783 | 0.29495 |  | 0.28885 | 0.2909 | 0.34171 | 0.29607
AE305 | 0.33946 | 0.29749 | 0.29495 |  | 0.29046 | 0.2909 | 0.33927 | 0.29198
AE306 | 0.33921 | 0.29727 | 0.29495 |  | 0.28884 | 0.2909 | 0.33905 | 0.29404
AE326 | 0.33921 | 0.29727 | 0.29495 |  | 0.28881 | 0.2909 | 0.33911 | 0.29505
AE345 | 0.33956 | 0.29758 | 0.29495 |  | 0.29112 | 0.2909 | 0.33943 | 0.29178
AE401
AE403 | 0.0049809 | 0.030526 | 0.004395 |  | 0.0038467 | 0.0117 | 0.0048549
AE404 | 0.10655 | 0.11411 | 0.10173 |  | 0.090258 | 0.0986 | 0.10623
AE405 | 0.0049578 | 0.0068611 | 0.004371 |  | 0.0037075 | 0.0117 | 0.0048189
AE406 | 0.0048953 | 0.0067188 | 0.004377 |  | 0.0031146 | 0.0117 | 0.0047643
AE426 | 0.0048953 | 0.0067188 | 0.004377 |  | 0.0031131 | 0.0116 | 0.0047598
AE445 | 0.0049631 | 0.0068735 | 0.004371 |  | 0.0036902 | 0.0117 | 0.0048202

## Delta Tables 1
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.2
Example Results for Section 11, Airside HVAC BESTEST Cases AE301 through AE445
Table B16.7.2-30. CV/VAV Delta Preheat Coil Load, CV - VAV (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 - AE401 | -7.3127 | -7.2782 | -6.73 | -7.0293 | -6.7682 | -6.804 | -7.3112
AE303 - AE403 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE304 - AE404 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE305 - AE405 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE306 - AE406 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE326 - AE426 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE345 - AE445 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table B16.7.2-31. CV/VAV Delta Sensible Cooling Coil Load, CV - VAV (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 - AE401 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE303 - AE403 | 5.2774 | 5.2419 | 5.0162 | 5.0177 | 5.0777 | 5.084 | 5.278
AE304 - AE404 | 2.9212 | 2.8821 | 2.6085 | 2.431 | 2.7857 | 2.701 | 2.9287
AE305 - AE405 | 5.2806 | 5.2447 | 5.0374 | 4.8149 | 5.1017 | 5.084 | 5.2824
AE306 - AE406 | 5.2857 | 5.2594 | 5.0718 | 4.9174 | 5.1602 | 5.085 | 5.2853
AE326 - AE426 | 4.867 | 4.7915 | 4.5396 | 4.5892 | 4.7066 | 4.58 | 4.8855
AE345 - AE445 | 5.5454 | 5.5247 | 5.277 | 5.115 | 5.3645 | 5.369 | 5.5625
Table B16.7.2-32. CV/VAV Delta Latent Cooling Coil Load, CV - VAV (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 - AE401 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE303 - AE403 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE304 - AE404 | 0.33412 | 0.32027 | 0.43027 | 0.29717 | 0.30444 | 0.316 | 0.34014
AE305 - AE405 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE306 - AE406 | 0.85526 | 0.83731 | 1.1349 | 0.939 | 0.90886 | 0.882 | 0.85438
AE326 - AE426 | 7.0651 | 7.0787 | 7.2465 | 6.5238 | 7.1418 | 7.102 | 7.0857
AE345 - AE445 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table B16.7.2-33. CV/VAV Delta Total Cooling Coil Load, CV - VAV (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
Test case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
AE301 - AE401 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE303 - AE403 | 5.2774 | 5.2419 | 5.0162 | 5.0177 | 5.0777 | 5.084 | 5.278
AE304 - AE404 | 3.2553 | 3.2024 | 3.0388 | 2.7282 | 3.0902 | 3.017 | 3.2689
AE305 - AE405 | 5.2806 | 5.2447 | 5.0374 | 4.8149 | 5.1017 | 5.084 | 5.2824
AE306 - AE406 | 6.141 | 6.0968 | 6.2066 | 5.8564 | 6.0691 | 5.968 | 6.1397
AE326 - AE426 | 11.9321 | 11.8702 | 11.7862 | 11.113 | 11.8484 | 11.682 | 11.9712
AE345 - AE445 | 5.5454 | 5.5247 | 5.277 | 5.115 | 5.3645 | 5.369 | 5.5625

## Delta Tables 2
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.2
Example Results for Section 11, Airside HVAC BESTEST Cases AE301 through AE445
Table B16.7.2-34. CV Delta Cooling Coil Load, Economizer Operation (kWh/h)
|  |  | QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
| Test case | Load | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
| AE345-AE305 | Total Cooling | 0.32005 | 0.33471 | 0.28782 | 0.35637 | 0.31021 | 0.334 | 0.33386 | 0.33699
|  | Sensible Cooling | 0.32005 | 0.33471 | 0.28782 | 0.35637 | 0.31021 | 0.334 | 0.33386 | 0.33699
|  | Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AE326 - AE306 | Total Cooling | 6.3983 | 6.3814 | 6.1912 | 5.9124 | 6.2871 | 6.251 | 6.4173 | 6.3682
|  | Sensible Cooling | -0.46026 | -0.51867 | -0.58455 | -0.36605 | -0.49552 | -0.556 | -0.44441 | -0.56609
|  | Latent Cooling | 6.8586 | 6.9001 | 6.7757 | 6.2785 | 6.7827 | 6.808 | 6.8617 | 6.9343
Table B16.7.2-35. VAV Delta Cooling Coil Load, Economizer Operation (kWh/h)
|  |  | QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | TRNSYS | OpenSimula
| Test case | Load | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | TESS | US
| AE445-AE405 | Total Cooling | 0.055217 | 0.054705 | 0.048245 | 0.05627 | 0.047365 | 0.049 | 0.053834
|  | Sensible Cooling | 0.055217 | 0.054705 | 0.048245 | 0.05627 | 0.047365 | 0.049 | 0.053834
|  | Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AE426 - AE406 | Total Cooling | 0.60713 | 0.60799 | 0.61163 | 0.65589 | 0.50783 | 0.537 | 0.5858
|  | Sensible Cooling | -0.041587 | -0.050749 | -0.052419 | -0.037806 | -0.041867 | -0.051 | -0.044634
|  | Latent Cooling | 0.64871 | 0.65874 | 0.66405 | 0.6937 | 0.54969 | 0.588 | 0.63044
r

## Detailed Location Results
User-definable chart to look at diagnostic results. Allows selection of test case and diagnostic variable; see Cells B4, B5 (instructions in Cells C4, C5). Displays selected case and diagnostic value for all programs by system location. For selection of viewed program results, see Cells A8-A20, A42-A54 (instructions in Cell A4).
Output spreadsheet for Airside HVAC BESTEST
Aggregator Sheet - Detailed Location Results
| AE301 | <== Select Case | Desc: | AE301 CV, Heating, OD/OWB = -29.00/-29.00 °C
| Dry Bulb Temperature (°C) | <== Select Variable | Title | AE301 CV, Heating, OD/OWB = -29.00/-29.00 °C Dry Bulb Temperature (°C)
[16 empty] | Dry Bulb Temperature (°C) | 1
InOut | Tab Name | [12 empty] | OFFSETS |  | Humidity Ratio (g/gda) | 2
1 | QAS | [14 empty] | Specific Volume (L/kgda) | 3
1 | DEEAP | [14 empty] | Enthalpy (J/gda) | 4
1 | DeST | [12 empty] | Summary Outputs | Detailed Outputs | Mass Flow Rate (kgda/s) | 5
1 | DOE22 | [11 empty] | AE301 | 77 | 77
1 | Eplus | [11 empty] | AE303 | 78 | 82
1 | IES-VE | [11 empty] | AE304 | 79 | 87
1 | TRNSYS | [11 empty] | AE305 | 80 | 92
0 | YourData | [11 empty] | AE306 | 81 | 97
0 | Blank | [11 empty] | AE326 | 82 | 102
0 | Blank | [11 empty] | AE345 | 83 | 107
0 | Blank | [11 empty] | AE401 | 125 | 125
0 | Blank | [11 empty] | AE403 | 126 | 130
0 | Blank | [11 empty] | AE404 | 127 | 135
[13 empty] | AE405 | 128 | 140
[13 empty] | AE406 | 129 | 145
[13 empty] | AE426 | 130 | 150
[13 empty] | AE445 | 131 | 155
Table Below
*
*
*
*
\/
|  |  | Results Offset ==> | 77 | Results Row ==> | 1 |  | Result Sets ==> | #N/A | Ret Fan Exists | TRUE
| Result Col Offset==> | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
| Air Loop Location==> | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
| Air Loop Location==> | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
InOut | Tab Name | Outdoor Air | Mixed Air | Preheat Coil Outlet | Cool Coil Outlet | Supply Air | Zone 1 Supply Air | Zone 2 Supply Air* | Zone 1 Air | Zone 2 Air* | Ret. Fan Inlet | Ret. Fan Outlet
1 | QAS | -29 | 3.4316 | 7.2222 | 7.2222 | 7.7838 | 29.2787 | 27.8228 | 21.1111 | 22.2222 | 21.6708 | 22.019
1 | DEEAP | -29 | 3.3982 | 7.2222 | 7.2222 | 7.7845 | 29.2883 | 27.8298 | 21.1111 | 22.2222 | 21.6708 | 21.9663
1 | DeST | -29 | 2.3874 | 7.22 | 7.22 | 7.8099 | 29.6699 | 28.084 | 21.111 | 22.222 | 21.7092 | 22.0042
1 | DOE22 | -29 | #N/A | 7.2222 | 7.2222 | 7.7778 | #N/A | #N/A | 21.1111 | 22.2222 | #N/A | 21.9444
1 | Eplus | -29 | 2.4185 | 7.22 | 7.22 | 7.8063 | 29.649 | 28.0886 | 21.1299 | 22.2485 | 21.6893 | 21.982
1 | IES-VE | -29 | 2.3582 | 7.22 | 7.22 | 7.8018 | 29.5754 | 28.026 | 21.1106 | 22.221 | 21.6658 | 21.9567
1 | TRNSYS | -29 | 3.4295 | 7.22 | 7.22 | 7.7815 | 29.27 | 27.81 | 21.1102 | 22.2171 | 21.6678 | 22.0159
0 | YourData | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Note on A7: Set to 0 to turn off result set.

## Aggregate Results
Output spreadsheet for Airside HVAC BESTEST
[5 empty] | DEEAP | DeST | DOE22 | EPlus | IES-VE
Aggregator Sheet - Collects data from Plots
Cooling Coil- Coil Outlet RH (RHcco) (%) |  | Results Column ==> | 11
OFFSETS
Cells B9:N9 contain the tab name of the results set. By changing the tab name all results for that column are changed and plot data updated. It is possible to change the order or plot multiple new results sets by changing the tab names. Plots currently only address through column I. To plot more than 9 results sets the plot ranges must be adjusted.
Tab Name==> | QAS | DEEAP | DeST | DOE22 | Eplus | IES-VE | TRNSYS | YourData | Blank | Blank | Blank | Blank | Blank |  | Summary Outputs | Detailed Outputs |  |  | Summary Output Columns | Detailed Output Columns
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 24.7331 | 24.7328 | #N/A | 23.9613 | 23.8906 | 24.65 | 24.6351 | 22.4118 | #N/A | #N/A | #N/A | #N/A | #N/A | AE301 | 77 | 77 | CAV Heat | AE301 CV, Heating, OD/OWB = -29.00/-29.00 °C | Zone 1 Sensible Heating Load (QZH1sensible) (kWh/h) | Variable
AE303 Dry Coil 15.5/-3.0 | 48.1495 | 47.6873 | 48.22 | 47.9247 | 47.4569 | 48.02 | 48.1783 | 49.1748 | #N/A | #N/A | #N/A | #N/A | #N/A | AE303 | 78 | 82 | CAV Dry Coil | AE303 CV, Dry Coil Cooling, OD/OWB = 15.50/7.21 °C | Zone 1 Sensible Cooling Load (QZC1sensible) (kWh/h) | Outdoor Air (oa)
AE304 Wet Coil 26.9/22.1 | 100 | 99.9992 | 95.49 | 100 | 99.1258 | 100 | 100 | 98.0574 | #N/A | #N/A | #N/A | #N/A | #N/A | AE304 | 79 | 87 | CAV Wet Coil | AE304 CV, Wet Coil Cooling, OD/OWB = 26.90/23.44 °C | Zone 1 Latent Load (QZ1latent) (kWh/h) | Mixed Air (ma)
AE305 Dry Coil 24.9/2.4 No Econo | 65.719 | 65.3364 | 65.84 | 65.5319 | 64.909 | 65.57 | 65.7465 | 66.2464 | #N/A | #N/A | #N/A | #N/A | #N/A | AE305 | 80 | 92 | CAV Dry Coil 2, No Econo | AE305 CV, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, No Economizer | Zone 2 Sensible Heating Load (QZH2sensible) (kWh/h) | Preheat Coil Outlet (pco)
AE306 Wet Coil 23.0/20.9 No Econo | 100 | 99.9992 | 96.21 | 100 | 99.2475 | 100 | 100 | 98.3662 | #N/A | #N/A | #N/A | #N/A | #N/A | AE306 | 81 | 97 | CAV Wet Coil 2, No Econo | AE306 CV, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, No Economizer | Zone 2 Sensible Cooling Load (QZC2sensible) (kWh/h) | Cool Coil Outlet (cco)
AE326 Wet Coil 23.0/20.9 DB Econo | 100 | 99.9992 | 98.89 | 100 | 99.9275 | 100 | 100 | 97.9418 | #N/A | #N/A | #N/A | #N/A | #N/A | AE326 | 82 | 102 | CAV Dry Coil 2, Dry Bulb Econo | AE326 CV, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, Dry Bulb Econo. | Zone 2 Latent Load (QZ2latent) (kWh/h) | Supply Air (sa)
AE345 Dry Coil 24.9/2.4 Enth. Eco | 51.0891 | 50.7067 | 51.33 | 51.1359 | 50.9944 | 51.1 | 51.1113 | 51.0089 | #N/A | #N/A | #N/A | #N/A | #N/A | AE345 | 83 | 107 | CAV Wet Coil 2, Enthalpy Econo | AE345 CV, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, Enthalpy Econo | Pre-Heating Coil Load (QHpreheat) (kWh/h) | Zone 1 Supply Air (z1s)
AE401 Heat -29.0/-29.0 | 4.1447 | 4.1474 | #N/A | 4.8015 | 4.1501 | 4.17 | 4.1464 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | AE401 | 125 | 125 | VAV Heat | AE401 VAV, Heating, OD/OWB = -29.00/-29.00 °C | Cooling Coil Loads- Sensible (QCsensible) (kWh/h) | Zone 2 Supply Air (z2s)
AE403 Dry Coil 15.5/-3.0 | 36.3949 | 36.0086 | 36.39 | 34.2896 | 35.8492 | 35.98 | 36.3722 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | AE403 | 126 | 130 | VAV Dry Coil | AE403 VAV, Dry Coil Cooling, OD/OWB = 15.50/7.21 °C | Cooling Coil Loads- Latent (QClatent) (kWh/h) | Zone 1 Air (z1)
AE404 Wet Coil 26.9/22.1 | 100 | 99.9992 | 97.24 | 100 | 98.7059 | 100 | 100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | AE404 | 127 | 135 | VAV Wet Coil | AE404 VAV, Wet Coil Cooling, OD/OWB = 26.90/23.44 °C | Cooling Coil Loads- Total (QCtotal) (kWh/h) | Zone 2 Air (z2)
AE405 Dry Coil 24.9/2.4 No Econo | 53.4629 | 53.1717 | 53.52 | 51.8548 | 52.7786 | 53.05 | 53.4325 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | AE405 | 128 | 140 | VAV Dry Coil 2, No Econo | AE405 VAV, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, No Economizer | Cooling Coil- Coil Outlet RH (RHcco) (%) | Return Fan Inlet (rfi)
AE406 Wet Coil 23.0/20.9 No Econo | 100 | 99.9992 | 99.38 | 100 | 99.7649 | 100 | 100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | AE406 | 129 | 145 | VAV Wet Coil 2, No Econo | AE406 VAV, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, No Economizer | Zone 1 Reheat Load (QH1reheat) (kWh/h) | Return Fan Outlet (rfo)
AE426 Wet Coil 23.0/20.9 DB Econo | 100 | 99.9992 | 99.58 | 100 | 99.9528 | 100 | 100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | AE426 | 130 | 150 | VAV Dry Coil 2, Dry Bulb Econo | AE426 VAV, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, Dry Bulb Econo. | Zone 2 Reheat Load (QH2reheat) (kWh/h)
AE445 Dry Coil 24.9/2.4 Enth. Eco | 49.575 | 49.2421 | 49.78 | 49.664 | 49.4632 | 49.58 | 49.5567 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | AE445 | 131 | 155 | VAV Wet Coil 2, Enthalpy Econo | AE445 VAV, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, Enthalpy Econo
Pre-Heating Coil Load (QHpreheat) (kWh/h) |  | Results Column ==> | 7
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 2.947 | 2.9697 | 3.58 | 3.7882 | 3.5747 | 3.647 | 2.9467 | 3.7747 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 10.2597 | 10.2479 | 10.31 | 10.8176 | 10.343 | 10.451 | 10.2578 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads- Sensible (QCsensible) (kWh/h) |  | Results Column ==> | 8
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 6.7354 | 6.7082 | 6.4595 | 6.4197 | 6.4764 | 6.483 | 6.7255 | 6.5489 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 10.3202 | 10.2556 | 10.0587 | 9.8897 | 10.1563 | 10.034 | 10.315 | 9.8644 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 9.3829 | 9.3496 | 9.1806 | 8.9287 | 9.1994 | 9.195 | 9.3734 | 9.1642 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 8.9211 | 8.8688 | 8.6987 | 8.5975 | 8.7437 | 8.652 | 8.9149 | 8.5615 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 8.4609 | 8.3501 | 8.1141 | 8.2315 | 8.2481 | 8.096 | 8.4705 | 7.9955 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 9.7029 | 9.6843 | 9.4684 | 9.2851 | 9.5096 | 9.529 | 9.7073 | 9.5012 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 7.399 | 7.3735 | 7.4502 | 7.4587 | 7.3706 | 7.333 | 7.3862 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 3.6354 | 3.6094 | 3.6269 | 3.6801 | 3.5834 | 3.567 | 3.6296 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 3.5938 | 3.5586 | 3.5745 | 3.6423 | 3.5416 | 3.516 | 3.5849 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads- Latent (QClatent) (kWh/h) |  | Results Column ==> | 9
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 6.2583 | 6.2947 | 7.0108 | 6.214 | 6.6217 | 6.629 | 6.2615 | 6.6051 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 5.4432 | 5.4441 | 6.1035 | 5.4338 | 5.7489 | 5.75 | 5.4435 | 5.7668 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 12.3018 | 12.3442 | 12.8792 | 11.7123 | 12.5316 | 12.558 | 12.3053 | 12.7011 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 5.9242 | 5.9745 | 6.5805 | 5.9168 | 6.3173 | 6.313 | 5.9214 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 4.5879 | 4.6068 | 4.9686 | 4.4948 | 4.84 | 4.868 | 4.5892 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 5.2366 | 5.2655 | 5.6327 | 5.1885 | 5.3897 | 5.456 | 5.2196 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads- Total (QCtotal) (kWh/h) |  | Results Column ==> | 10
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 6.7354 | 6.7082 | 6.4595 | 6.4197 | 6.4764 | 6.483 | 6.7255 | 6.5489 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 16.5785 | 16.5503 | 17.0695 | 16.1037 | 16.778 | 16.662 | 16.5765 | 16.4695 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 9.3829 | 9.3496 | 9.1806 | 8.9287 | 9.1994 | 9.195 | 9.3734 | 9.1642 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 14.3643 | 14.3129 | 14.8022 | 14.0314 | 14.4926 | 14.403 | 14.3584 | 14.3284 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 20.7626 | 20.6943 | 20.9933 | 19.9438 | 20.7797 | 20.654 | 20.7757 | 20.6966 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 9.7029 | 9.6843 | 9.4684 | 9.2851 | 9.5096 | 9.529 | 9.7073 | 9.5012 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 13.3232 | 13.348 | 14.0307 | 13.3755 | 13.6879 | 13.645 | 13.3076 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 8.2233 | 8.2162 | 8.5955 | 8.1749 | 8.4235 | 8.435 | 8.2187 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 8.8305 | 8.8241 | 9.2072 | 8.8308 | 8.9313 | 8.972 | 8.8045 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Reheat Load (QH1reheat) (kWh/h) |  | Results Column ==> | 12
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 7.7129 | 7.7075 | 7.4721 | 7.706 | 7.5057 | 7.539 | 7.7093 | 7.7894 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 2.2584 | 2.2547 | 2.1363 | 2.15 | 2.1827 | 2.188 | 2.2552 | 2.245 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.99332 | 0.98884 | 0.85904 | 0.79774 | 0.94208 | 0.915 | 0.99153 | 0.84482 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 2.2598 | 2.2561 | 2.1367 | 2.0723 | 2.193 | 2.188 | 2.2567 | 2.1752 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 2.2625 | 2.2588 | 2.1374 | 2.1107 | 2.2136 | 2.188 | 2.2618 | 2.1522 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 2.2625 | 2.2588 | 2.1374 | 2.1256 | 2.2141 | 2.188 | 2.2668 | 2.1398 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 2.2587 | 2.255 | 2.1374 | 2.0887 | 2.1849 | 2.188 | 2.2607 | 2.1776 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 4.4994 | 4.4963 | 4.5019 | 4.5839 | 4.5034 | 4.524 | 4.4895 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Reheat Load (QH2reheat) (kWh/h) |  | Results Column ==> | 13
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 8.3889 | 8.3822 | 8.0774 | 8.3763 | 8.1309 | 8.17 | 8.3843 | 8.4642 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 2.4572 | 2.4515 | 2.3 | 2.3194 | 2.3607 | 2.366 | 2.4545 | 2.4364 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 1.519 | 1.5135 | 1.3509 | 1.2681 | 1.4552 | 1.419 | 1.5236 | 1.3315 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 2.4589 | 2.4532 | 2.3017 | 2.2232 | 2.3739 | 2.366 | 2.4562 | 2.351 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 2.4624 | 2.4568 | 2.3004 | 2.2695 | 2.4005 | 2.366 | 2.4621 | 2.3206 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 2.4624 | 2.4568 | 2.3005 | 2.2886 | 2.4012 | 2.366 | 2.4678 | 2.3046 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 2.4575 | 2.4518 | 2.3005 | 2.2414 | 2.3635 | 2.366 | 2.461 | 2.3541 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 4.8772 | 4.8725 | 4.891 | 5.0147 | 4.9022 | 4.926 | 4.8689 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Detailed Outputs
Outdoor Air Temp |  | Results Column ==> | 1 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Humidity Ratio |  | Results Column ==> | 1 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | 0.00025893 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029359 | 0.0029317 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016774 | 0.016766 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.0044783 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.01556 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.01556 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.0044783 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029359 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016774 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Humidity Ratio (just for 5 cases)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE305 Dry Coil 24.9/2.4 No Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.0044783 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.01556 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015556 | 0.01556 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.0044783 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Mass Flow Rat |  | Results Column ==> | 1 |  | Results Row Offset==> | 4
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.28139 | 0.28143 | 0.28316 | 0.29649 | 0.28418 | 0.28316 | 0.2814 | 0.29647 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.27809 | 0.27814 | 0.28316 | 0.28151 | 0.28418 | 0.28316 | 0.27808 | 0.28996 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.27554 | 0.27557 | 0.28316 | 0.2735 | 0.28418 | 0.28316 | 0.27553 | 0.28179 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.2774 | 0.27745 | 0.28316 | 0.27741 | 0.28418 | 0.28316 | 0.27739 | 0.28575 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.27605 | 0.27609 | 0.28316 | 0.27538 | 0.28418 | 0.28316 | 0.27604 | 0.28374 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.74832 | 0.74842 | 0.73624 | 0.71372 | 0.73888 | 0.73624 | 0.74833 | 0.73521 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.75353 | 0.75367 | 0.73624 | 0.72169 | 0.73888 | 0.73624 | 0.75354 | 0.74345 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.28139 | 0.28143 | 0.28316 | 0.29707 | 0.28418 | 0.28316 | 0.2814 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.27809 | 0.27814 | 0.28316 | 0.28597 | 0.28418 | 0.28316 | 0.27808 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.27533 | 0.27537 | 0.28316 | 0.27289 | 0.28418 | 0.28316 | 0.27532 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.2774 | 0.27745 | 0.28316 | 0.27761 | 0.28418 | 0.28316 | 0.27739 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.27552 | 0.27556 | 0.28316 | 0.27474 | 0.28418 | 0.28316 | 0.27552 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.33213 | 0.33253 | 0.33835 | 0.32941 | 0.33144 | 0.33354 | 0.33133 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.33495 | 0.33538 | 0.33832 | 0.33586 | 0.33427 | 0.33354 | 0.33411 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Temperature |  | Results Column ==> | 5 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 7.7838 | 7.7845 | 7.8099 | 7.7778 | 7.8063 | 7.8018 | 7.7815 | 7.7835 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 12.7778 | 12.7778 | 12.7948 | 12.7778 | 12.7804 | 12.7808 | 12.7861 | 12.78 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 12.7778 | 12.7778 | 12.7946 | 12.8333 | 12.7797 | 12.7808 | 12.7819 | 12.78 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 12.7778 | 12.7778 | 12.7948 | 12.8889 | 12.7806 | 12.7808 | 12.7841 | 12.78 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 12.7778 | 12.7778 | 12.7658 | 12.7778 | 12.7804 | 12.7808 | 12.7843 | 12.78 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 12.7778 | 12.7778 | 12.7937 | 12.7778 | 12.7801 | 12.7808 | 12.7705 | 12.78 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 12.7778 | 12.7778 | 12.7948 | 12.7778 | 12.78 | 12.7808 | 12.7711 | 12.78 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 7.2968 | 7.3083 | 7.3073 | 7.2778 | 7.2901 | 7.3103 | 7.2949 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 12.7778 | 12.7778 | 12.795 | 12.7778 | 12.78 | 12.7795 | 12.7822 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 12.7778 | 12.7778 | 12.7916 | 12.7778 | 12.7797 | 12.7846 | 12.7811 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 12.7778 | 12.7778 | 12.795 | 12.7778 | 12.7802 | 12.7795 | 12.7825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 12.7778 | 12.7778 | 12.7939 | 12.7778 | 12.78 | 12.7795 | 12.7709 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 12.7778 | 12.7778 | 12.782 | 12.7778 | 12.7801 | 12.7795 | 12.7822 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 12.7778 | 12.7778 | 12.795 | 12.7778 | 12.7802 | 12.7795 | 12.7825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Humidity Ratio |  | Results Column ==> | 5 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.0015483 | 0.0015484 | 0.0015343 | 0.0015 | 0.0014957 | 0.001549 | 0.0015419 | 0.0014025 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.0042307 | 0.0041899 | 0.0042354 | 0.0042 | 0.0041681 | 0.004234 | 0.0042356 | 0.0043208 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.0088518 | 0.008852 | 0.0084426 | 0.0089 | 0.0087725 | 0.008891 | 0.0088543 | 0.0086662 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.0057889 | 0.0057551 | 0.0057974 | 0.0058 | 0.0057157 | 0.005795 | 0.0057938 | 0.0058316 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.0088518 | 0.008852 | 0.0084916 | 0.0089 | 0.0087839 | 0.008888 | 0.0088557 | 0.0086963 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.0088518 | 0.008852 | 0.0087474 | 0.0089 | 0.0088448 | 0.008909 | 0.0088476 | 0.0086571 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.0044807 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.00025893 | 0.00025861 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0032906 | 0.0032519 | 0.0032876 | 0.0031 | 0.003241 | 0.003265 | 0.0032889 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.0090147 | 0.0090036 | 0.0087492 | 0.009 | 0.0088944 | 0.009056 | 0.009017 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0048458 | 0.004814 | 0.004851 | 0.0047 | 0.0047837 | 0.004826 | 0.004835 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.009126 | 0.0091159 | 0.0090684 | 0.0092 | 0.0091064 | 0.009175 | 0.0091221 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.009126 | 0.0091159 | 0.0090802 | 0.0092 | 0.0091238 | 0.009184 | 0.0091292 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Specific Volume |  | Results Column ==> | 5 |  | Results Row Offset==> | 2
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 797.8282 | 797.7263 | 833.33 | #N/A | 830.3519 | #N/A | 793.9174 | 797.6468 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 815.504 | 815.3446 | 833.33 | #N/A | 830.3519 | #N/A | 811.5517 | 815.634 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 821.5223 | 821.4151 | 833.33 | #N/A | 830.3519 | #N/A | 817.5256 | 821.2933 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 817.5333 | 817.3825 | 833.33 | #N/A | 830.3519 | #N/A | 813.5654 | 817.6016 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 821.5223 | 821.4151 | 833.33 | #N/A | 830.3519 | #N/A | 817.5341 | 821.3324 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 821.5223 | 821.4151 | 833.33 | #N/A | 830.3519 | #N/A | 817.4842 | 821.2814 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 815.8428 | 815.6925 | 833.33 | #N/A | 830.3519 | #N/A | 811.8397 | 815.8422 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 794.7981 | 794.7275 | 833.33 | #N/A | 830.3519 | #N/A | 794.2783 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 814.2796 | 814.1232 | 833.33 | #N/A | 830.3519 | #N/A | 813.5066 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 821.7345 | 821.6126 | 833.33 | #N/A | 830.3519 | #N/A | 819.6593 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 816.3051 | 816.1571 | 833.33 | #N/A | 830.3519 | #N/A | 815.5201 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 821.8794 | 821.7587 | 833.33 | #N/A | 830.3519 | #N/A | 821.0663 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 821.8794 | 821.7587 | 833.33 | #N/A | 830.3519 | #N/A | 821.1102 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 815.8428 | 815.6925 | 833.33 | #N/A | 830.3519 | #N/A | 815.0746 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Enthalpy |  | Results Column ==> | 5 |  | Results Row Offset==> | 3
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 11.726 | #N/A | 11.71 | #N/A | 11.6064 | #N/A | 11.7069 | 11.3582 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 23.5371 | #N/A | 23.55 | #N/A | 23.3653 | #N/A | 23.5569 | 23.7658 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 35.2043 | #N/A | 34.16 | #N/A | 34.9895 | #N/A | 35.2138 | 34.737 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 27.4712 | #N/A | 27.49 | #N/A | 27.2729 | #N/A | 27.489 | 27.5803 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 35.2043 | #N/A | 34.26 | #N/A | 35.0189 | #N/A | 35.2197 | 34.8128 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 35.2043 | #N/A | 34.93 | #N/A | 35.1723 | #N/A | 35.185 | 34.7138 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 24.194 | #N/A | 24.24 | #N/A | 24.155 | #N/A | 24.186 | 24.1695 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 7.9923 | #N/A | 8 | #N/A | 7.9766 | #N/A | 7.9897 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 21.1635 | #N/A | 21.16 | #N/A | 21.0244 | #N/A | 21.1625 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 35.6156 | #N/A | 34.93 | #N/A | 35.2972 | #N/A | 35.6235 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 25.0901 | #N/A | 25.1 | #N/A | 24.9195 | #N/A | 25.0664 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 35.8965 | #N/A | 35.74 | #N/A | 35.8327 | #N/A | 35.8787 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 35.8965 | #N/A | 35.76 | #N/A | 35.8769 | #N/A | 35.908 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 24.194 | #N/A | 24.24 | #N/A | 24.1552 | #N/A | 24.1977 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Mass Flow Rate |  | Results Column ==> | 5 |  | Results Row Offset==> | 4
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.77054 | 0.77064 | 0.73624 | 0.77088 | 0.73888 | 0.73624 | 0.77055 | 0.77082 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.75384 | 0.75399 | 0.73624 | 0.73193 | 0.73888 | 0.73624 | 0.7538 | 0.75391 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.74832 | 0.74842 | 0.73624 | 0.71109 | 0.73888 | 0.73624 | 0.74829 | 0.73267 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.75197 | 0.75211 | 0.73624 | 0.72126 | 0.73888 | 0.73624 | 0.75194 | 0.74296 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.74832 | 0.74842 | 0.73624 | 0.716 | 0.73888 | 0.73624 | 0.74829 | 0.73774 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.74832 | 0.74842 | 0.73624 | 0.71372 | 0.73888 | 0.73624 | 0.74833 | 0.73521 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.75353 | 0.75367 | 0.73624 | 0.72169 | 0.73888 | 0.73624 | 0.75354 | 0.74345 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.28139 | 0.28143 | 0.28316 | 0.29707 | 0.28418 | 0.28316 | 0.2814 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.33569 | 0.33612 | 0.3385 | 0.33688 | 0.3351 | 0.33354 | 0.33495 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.53919 | 0.53988 | 0.54925 | 0.53541 | 0.53845 | 0.54137 | 0.53882 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.33473 | 0.33516 | 0.33832 | 0.33591 | 0.33415 | 0.33354 | 0.33393 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.33213 | 0.33253 | 0.33835 | 0.32968 | 0.33145 | 0.33354 | 0.33137 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.33213 | 0.33253 | 0.33835 | 0.32941 | 0.33144 | 0.33354 | 0.33133 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.33495 | 0.33538 | 0.33832 | 0.33586 | 0.33427 | 0.33354 | 0.33411 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Air Temperature |  | Results Column ==> | 8 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 21.1111 | 21.1111 | 21.111 | 21.1111 | 21.1299 | 21.1106 | 21.1102 | 21.111 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3285 | 23.333 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 23.8889 | 23.8889 | 23.889 | 23.8889 | 23.8914 | 23.8893 | 23.8806 | 23.889 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3269 | 23.333 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3339 | 23.333 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.3337 | 23.333 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3385 | 23.3314 | 23.328 | 23.333 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 21.1111 | 21.1111 | 21.111 | 21.1111 | 21.1452 | 21.1103 | 21.1151 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3302 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 23.8889 | 23.8889 | 23.889 | 23.8889 | 23.9001 | 23.8934 | 23.8829 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3319 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.318 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3286 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 23.3333 | 23.3333 | 23.333 | 23.3333 | 23.3441 | 23.3321 | 23.3321 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Supply Air Temperature |  | Results Column ==> | 6 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 29.2787 | 29.2883 | 29.6699 | #N/A | 29.649 | 29.5754 | 29.27 | 29.5476 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 19.1796 | 19.1761 | 19.05 | #N/A | 19.1013 | 19.1006 | 19.18 | 19.1935 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 15.5904 | 15.5808 | 15.3101 | #N/A | 15.485 | 15.4247 | 15.59 | 15.2634 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 19.1811 | 19.1778 | 19.0515 | #N/A | 19.1133 | 19.1006 | 19.18 | 19.0856 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 19.1841 | 19.1807 | 19.0246 | #N/A | 19.1369 | 19.1006 | 19.19 | 19.0631 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 19.1841 | 19.1807 | 19.0525 | #N/A | 19.1373 | 19.1006 | 19.19 | 19.0484 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 19.1799 | 19.1765 | 19.0515 | #N/A | 19.1037 | 19.1006 | 19.18 | 19.0884 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 46.92 | 46.9483 | 46.8548 | #N/A | 46.6969 | 46.5047 | 46.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 12.7778 | 12.7777 | 12.795 | #N/A | 12.78 | 12.7795 | 12.7822 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 12.7778 | 12.7777 | 12.7916 | #N/A | 12.7808 | 12.7846 | 12.7878 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 12.7778 | 12.7777 | 12.795 | #N/A | 12.7802 | 12.7795 | 12.7825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 12.7778 | 12.7777 | 12.7939 | #N/A | 12.7899 | 12.7795 | 12.7709 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 12.7778 | 12.7777 | 12.782 | #N/A | 12.79 | 12.7795 | 12.7822 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 12.7778 | 12.7778 | 12.795 | #N/A | 12.7802 | 12.7795 | 12.7825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Supply Air Humidity Ratio |  | Results Column ==> | 6 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.0015483 | 0.0015484 | 0.0015343 | 0.0015 | 0.0014957 | 0.001549 | 0.0015419 | 0.0014025 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.0042307 | 0.0041899 | 0.0042354 | 0.0042 | 0.0041681 | 0.004234 | 0.0042356 | 0.0043208 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.0088518 | 0.008852 | 0.0084426 | 0.0089 | 0.0087725 | 0.008891 | 0.0088543 | 0.0086662 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.0057889 | 0.0057551 | 0.0057974 | 0.0058 | 0.0057157 | 0.005795 | 0.0057938 | 0.0058316 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.0088518 | 0.008852 | 0.0084916 | 0.0089 | 0.0087839 | 0.008888 | 0.0088557 | 0.0086963 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.0088518 | 0.008852 | 0.0087474 | 0.0089 | 0.0088448 | 0.008909 | 0.0088476 | 0.0086571 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.0044807 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.00025893 | 0.00025861 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00026343 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0032906 | 0.0032519 | 0.0032876 | 0.0031 | 0.003241 | 0.003265 | 0.0032889 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.0090147 | 0.0090036 | 0.0087492 | 0.009 | 0.0088944 | 0.009056 | 0.009021 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0048458 | 0.0048143 | 0.004851 | 0.0047 | 0.0047837 | 0.004826 | 0.004835 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.009126 | 0.0091159 | 0.0090684 | 0.0092 | 0.0091018 | 0.009175 | 0.0091221 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.009126 | 0.0091159 | 0.0090802 | 0.0092 | 0.009124 | 0.009184 | 0.0091292 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Air Temperature |  | Results Column ==> | 9 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 22.2222 | 22.2222 | 22.222 | 22.2222 | 22.2485 | 22.221 | 22.2171 | 22.222 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.442 | 24.4389 | 24.444 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 25 | 25 | 25 | 25 | 25.0047 | 25.001 | 25.0027 | 25 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.4419 | 24.4367 | 24.444 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.4419 | 24.4427 | 24.444 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.442 | 24.4424 | 24.444 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4517 | 24.4419 | 24.4382 | 24.444 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 22.2222 | 22.2222 | 22.222 | 22.2222 | 22.2593 | 22.2208 | 22.2211 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4608 | 24.4431 | 24.4386 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 25 | 25 | 25 | 25 | 25.0168 | 25.0043 | 24.9989 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4431 | 24.4401 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4432 | 24.431 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4431 | 24.4416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 24.4444 | 24.4444 | 24.444 | 24.4444 | 24.4607 | 24.4431 | 24.442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Supply Air Temperature |  | Results Column ==> | 7 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 27.8228 | 27.8298 | 28.084 | #N/A | 28.0886 | 28.026 | 27.81 | 28.0547 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 18.7479 | 18.7408 | 18.57 | #N/A | 18.6401 | 18.637 | 18.75 | 18.7458 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 16.4644 | 16.4551 | 16.1852 | #N/A | 16.3615 | 16.2939 | 16.48 | 16.135 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 18.75 | 18.7428 | 18.572 | #N/A | 18.6566 | 18.6371 | 18.75 | 18.6216 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 18.7541 | 18.747 | 18.5398 | #N/A | 18.6889 | 18.6371 | 18.76 | 18.5869 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 18.7541 | 18.747 | 18.5677 | #N/A | 18.6896 | 18.637 | 18.76 | 18.5668 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 18.7483 | 18.7411 | 18.572 | #N/A | 18.6434 | 18.6371 | 18.75 | 18.6255 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 36.0391 | 36.0548 | 35.9521 | #N/A | 35.8886 | 35.7662 | 35.9884 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 12.7778 | 12.7777 | 12.795 | #N/A | 12.78 | 12.7795 | 12.7822 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 12.7778 | 12.7777 | 12.7916 | #N/A | 12.7808 | 12.7846 | 12.7878 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 12.7778 | 12.7777 | 12.795 | #N/A | 12.7802 | 12.7795 | 12.7825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 12.7778 | 12.7777 | 12.7939 | #N/A | 12.7899 | 12.7795 | 12.7709 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 12.7778 | 12.7777 | 12.782 | #N/A | 12.79 | 12.7795 | 12.7822 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 12.7778 | 12.7778 | 12.795 | #N/A | 12.7802 | 12.7795 | 12.7825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Supply Air Humidity Ratio |  | Results Column ==> | 7 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.0015483 | 0.0015484 | 0.0015343 | 0.0015 | 0.0014957 | 0.001549 | 0.0015419 | 0.0014025 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.0042307 | 0.0041899 | 0.0042354 | 0.0042 | 0.0041681 | 0.004234 | 0.0042356 | 0.0043208 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.0088518 | 0.008852 | 0.0084426 | 0.0089 | 0.0087725 | 0.008891 | 0.0088543 | 0.0086662 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.0057889 | 0.0057551 | 0.0057974 | 0.0058 | 0.0057157 | 0.005795 | 0.0057938 | 0.0058316 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.0088518 | 0.008852 | 0.0084916 | 0.0089 | 0.0087839 | 0.008888 | 0.0088557 | 0.0086963 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.0088518 | 0.008852 | 0.0087474 | 0.0089 | 0.0088448 | 0.008909 | 0.0088476 | 0.0086571 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | 0.0044807 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.00025893 | 0.00025861 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00025893 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0032906 | 0.0032519 | 0.0032876 | 0.0031 | 0.003241 | 0.003265 | 0.0032889 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.0090147 | 0.0090036 | 0.0087492 | 0.009 | 0.0088944 | 0.009056 | 0.009021 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0048458 | 0.0048143 | 0.004851 | 0.0047 | 0.0047837 | 0.004826 | 0.004835 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.009126 | 0.0091159 | 0.0090684 | 0.0092 | 0.0091018 | 0.009175 | 0.0091221 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.009126 | 0.0091159 | 0.0090802 | 0.0092 | 0.009124 | 0.009184 | 0.0091292 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044909 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Outlet Air Temperature |  | Results Column ==> | 4 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 7.2222 | 7.2222 | 7.22 | 7.2222 | 7.22 | 7.22 | 7.22 | 7.2206 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 12.2066 | 12.2059 | 12.2049 | 12.1667 | 12.197 | 12.199 | 12.215 | 12.2045 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 12.2072 | 12.2065 | 12.2047 | 12.2222 | 12.2012 | 12.199 | 12.2114 | 12.1878 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 12.2068 | 12.2061 | 12.2049 | 12.2778 | 12.1989 | 12.199 | 12.2132 | 12.196 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 12.2072 | 12.2065 | 12.1759 | 12.2222 | 12.2019 | 12.199 | 12.2138 | 12.1919 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 12.2072 | 12.2065 | 12.2038 | 12.2222 | 12.2017 | 12.199 | 12.2 | 12.1899 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 12.2066 | 12.2059 | 12.2049 | 12.2222 | 12.197 | 12.199 | 12.2 | 12.1964 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 7.2222 | 7.2222 | 7.22 | 7.2222 | 7.2031 | 7.22 | 7.22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 12.6643 | 12.6466 | 12.6699 | 12.6667 | 12.6598 | 12.66 | 12.6692 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 12.4805 | 12.4612 | 12.4633 | 12.4444 | 12.4725 | 12.47 | 12.491 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 12.6644 | 12.6468 | 12.6704 | 12.6667 | 12.661 | 12.66 | 12.6697 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 12.6647 | 12.6472 | 12.6693 | 12.6667 | 12.6637 | 12.66 | 12.6584 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 12.6647 | 12.6472 | 12.6574 | 12.6667 | 12.6638 | 12.66 | 12.67 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 12.6644 | 12.6519 | 12.6704 | 12.6667 | 12.6608 | 12.66 | 12.67 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Humidity Ratio |  | Results Column ==> | 8 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.0021971 | 0.0021972 | 0.0022251 | #N/A | 0.0021723 | 0.002253 | 0.0021868 | 0.0020231 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.0048927 | 0.0048518 | 0.0049298 | #N/A | 0.0048436 | 0.004938 | 0.0048998 | 0.0050918 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.0095185 | 0.0095186 | 0.00914 | #N/A | 0.0094477 | 0.009595 | 0.0095252 | 0.0093595 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.0064526 | 0.0064187 | 0.0064918 | #N/A | 0.0063912 | 0.006499 | 0.0064597 | 0.0065783 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.0095187 | 0.0095189 | 0.00919 | #N/A | 0.0094593 | 0.009592 | 0.0095248 | 0.0093843 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.0095187 | 0.0095189 | 0.0094417 | #N/A | 0.0095202 | 0.009613 | 0.0095166 | 0.0093477 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0051532 | 0.0051194 | 0.0052044 | #N/A | 0.0051565 | 0.005212 | 0.0051553 | 0.0051637 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.002304 | 0.0023034 | 0.0023324 | #N/A | 0.0022887 | 0.002374 | 0.0022691 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0049701 | 0.00493 | 0.0049958 | #N/A | 0.0049254 | 0.005021 | 0.0049882 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.0099076 | 0.0098953 | 0.0096515 | #N/A | 0.009788 | 0.00998 | 0.0099213 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0065301 | 0.006497 | 0.0065572 | #N/A | 0.0064728 | 0.006582 | 0.0065372 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.010823 | 0.010812 | 0.010775 | #N/A | 0.010803 | 0.010931 | 0.010838 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.010823 | 0.010812 | 0.010787 | #N/A | 0.010825 | 0.01094 | 0.010844 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0061741 | 0.0061387 | 0.0062162 | #N/A | 0.0061691 | 0.006264 | 0.0061921 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Humidity Ratio |  | Results Column ==> | 9 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.0023817 | 0.0023819 | 0.0024213 | #N/A | 0.0023649 | 0.002454 | 0.0023719 | 0.0022113 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.0050812 | 0.0050403 | 0.0051345 | #N/A | 0.0050359 | 0.005139 | 0.0050898 | 0.0052843 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.0097082 | 0.0097084 | 0.00934 | #N/A | 0.00964 | 0.009796 | 0.0097162 | 0.0095576 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.0066415 | 0.0066076 | 0.0066965 | #N/A | 0.0065835 | 0.0067 | 0.0066501 | 0.0067736 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.0097086 | 0.0097087 | 0.00939 | #N/A | 0.0096517 | 0.009793 | 0.0097161 | 0.009581 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.0097086 | 0.0097087 | 0.00965 | #N/A | 0.0097126 | 0.009814 | 0.009708 | 0.0095451 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.0053417 | 0.0053078 | 0.0054091 | #N/A | 0.0053488 | 0.005413 | 0.0053453 | 0.0053589 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.0023101 | 0.0023096 | 0.0023296 | #N/A | 0.0022872 | 0.002374 | 0.0022892 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0050294 | 0.0049886 | 0.0050706 | #N/A | 0.0049851 | 0.005084 | 0.0050489 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.010241 | 0.010229 | 0.0099979 | #N/A | 0.010124 | 0.010327 | 0.010261 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0065896 | 0.0065555 | 0.006633 | #N/A | 0.0065327 | 0.006645 | 0.006598 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.010883 | 0.010871 | 0.010849 | #N/A | 0.010863 | 0.010994 | 0.0109 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.010883 | 0.010871 | 0.010861 | #N/A | 0.010885 | 0.011003 | 0.010906 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0062336 | 0.0061973 | 0.006292 | #N/A | 0.006229 | 0.006327 | 0.006253 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Fan Temperature Rise (°C)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.5616 | 0.56226 | 0.5899 | 0.55556 | 0.58627 | 0.5818 | 0.56149 | 0.56288 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.57122 | 0.57189 | 0.5899 | 0.61111 | 0.58339 | 0.5818 | 0.57113 | 0.5755 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.5706 | 0.57126 | 0.5899 | 0.61111 | 0.5785 | 0.5818 | 0.5705 | 0.59219 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.57101 | 0.57168 | 0.5899 | 0.61111 | 0.58174 | 0.5818 | 0.57091 | 0.58399 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.5706 | 0.57126 | 0.5899 | 0.55556 | 0.57849 | 0.5818 | 0.5705 | 0.58812 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.5706 | 0.57126 | 0.5899 | 0.55556 | 0.57843 | 0.5818 | 0.57048 | 0.59014 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.57119 | 0.57185 | 0.5899 | 0.55556 | 0.58306 | 0.5818 | 0.57106 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.074611 | 0.086087 | 0.087254 | 0.055556 | 0.086922 | 0.0903 | 0.074852 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.1135 | 0.13116 | 0.1251 | 0.11111 | 0.1202 | 0.1195 | 0.11296 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.29723 | 0.31661 | 0.32831 | 0.33333 | 0.30715 | 0.3146 | 0.29011 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.11338 | 0.13101 | 0.12457 | 0.11111 | 0.11918 | 0.1195 | 0.11281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.11304 | 0.1306 | 0.12459 | 0.11111 | 0.11634 | 0.1195 | 0.11249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.11304 | 0.1306 | 0.12459 | 0.11111 | 0.11633 | 0.1195 | 0.11216 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.1134 | 0.12586 | 0.12457 | 0.11111 | 0.11933 | 0.1195 | 0.11252 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Return Fan Temperature Rise (°C)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.34819 | 0.29556 | 0.29495 | #N/A | 0.29272 | 0.2909 | 0.34804 | 0.2814 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.33958 | 0.2976 | 0.29495 | #N/A | 0.29128 | 0.2909 | 0.3394 | 0.28773 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.34187 | 0.29783 | 0.29495 | #N/A | 0.28885 | 0.2909 | 0.34171 | 0.29607 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.33946 | 0.29749 | 0.29495 | #N/A | 0.29046 | 0.2909 | 0.33927 | 0.29198 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.33921 | 0.29727 | 0.29495 | #N/A | 0.28884 | 0.2909 | 0.33905 | 0.29404 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.33921 | 0.29727 | 0.29495 | #N/A | 0.28881 | 0.2909 | 0.33911 | 0.29505 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.33956 | 0.29758 | 0.29495 | #N/A | 0.29112 | 0.2909 | 0.33943 | 0.29178 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0049809 | 0.030526 | 0.004395 | #N/A | 0.0038467 | 0.0117 | 0.0048549 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.10655 | 0.11411 | 0.10173 | #N/A | 0.090258 | 0.0986 | 0.10623 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0049578 | 0.0068611 | 0.004371 | #N/A | 0.0037075 | 0.0117 | 0.0048189 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.0048953 | 0.0067188 | 0.004377 | #N/A | 0.0031146 | 0.0117 | 0.0047643 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.0048953 | 0.0067188 | 0.004377 | #N/A | 0.0031131 | 0.0116 | 0.0047598 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0049631 | 0.0068735 | 0.004371 | #N/A | 0.0036902 | 0.0117 | 0.0048202 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Aggregate Coil Load (Heating and Cooling) |  | Results Column ==> |  |  | Results Row Offset==>
abs of sum of heating (negative) and cooling (positive)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 19.0488 | 19.0593 | 19.1295 | 19.8705 | 19.2113 | 19.356 | 19.0403 | 20.0283 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 11.4511 | 11.4144 | 10.8958 | 10.8891 | 11.0198 | 11.037 | 11.4352 | 11.2303 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 19.0908 | 19.0527 | 19.2794 | 18.1695 | 19.1753 | 18.996 | 19.0917 | 18.6459 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 14.1016 | 14.0589 | 13.6189 | 13.2243 | 13.7663 | 13.749 | 14.0864 | 13.6904 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 19.0892 | 19.0285 | 19.24 | 18.4116 | 19.1067 | 18.957 | 19.0823 | 18.8012 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 25.4875 | 25.4099 | 25.4312 | 24.358 | 25.395 | 25.208 | 25.5104 | 25.141 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 14.4191 | 14.391 | 13.9062 | 13.6152 | 14.0581 | 14.083 | 14.429 | 14.0329 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 19.6363 | 19.6167 | 19.7028 | 20.4162 | 19.7485 | 19.901 | 19.6163 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 13.3232 | 13.348 | 14.0307 | 13.3755 | 13.6879 | 13.645 | 13.3076 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 8.2233 | 8.2162 | 8.5955 | 8.1749 | 8.4235 | 8.435 | 8.2187 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 8.8305 | 8.8241 | 9.2072 | 8.8308 | 8.9313 | 8.972 | 8.8045 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Aggregate Sensible Coil Load (Heating and Cooling) |  | Results Column ==> |  |  | Results Row Offset==>
abs of sum of heating (negative) and cooling (positive)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 19.0488 | 19.0593 | 19.1295 | 19.8705 | 19.2113 | 19.356 | 19.0403 | 20.0283 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 11.4511 | 11.4144 | 10.8958 | 10.8891 | 11.0198 | 11.037 | 11.4352 | 11.2303 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 12.8325 | 12.7579 | 12.2686 | 11.9555 | 12.5536 | 12.368 | 12.8301 | 12.0407 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 14.1016 | 14.0589 | 13.6189 | 13.2243 | 13.7663 | 13.749 | 14.0864 | 13.6904 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 13.646 | 13.5844 | 13.1365 | 12.9778 | 13.3578 | 13.206 | 13.6388 | 13.0344 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 13.1857 | 13.0657 | 12.552 | 12.6457 | 12.8634 | 12.65 | 13.2051 | 12.4399 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 14.4191 | 14.391 | 13.9062 | 13.6152 | 14.0581 | 14.083 | 14.429 | 14.0329 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 19.6363 | 19.6167 | 19.7028 | 20.4162 | 19.7485 | 19.901 | 19.6163 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 1.458 | 1.4663 | 1.4433 | 1.4021 | 1.3987 | 1.399 | 1.4476 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 7.399 | 7.3735 | 7.4502 | 7.4587 | 7.3706 | 7.333 | 7.3862 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 4.1023 | 4.1049 | 4.1432 | 4.1138 | 4.0977 | 4.111 | 4.091 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 3.6354 | 3.6094 | 3.6269 | 3.6801 | 3.5834 | 3.567 | 3.6296 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 3.5938 | 3.5586 | 3.5745 | 3.6423 | 3.5416 | 3.516 | 3.5849 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 4.1575 | 4.1596 | 4.1914 | 4.1701 | 4.1451 | 4.16 | 4.1448 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Fraction
Fraction of supply air mass flow that is outdoor air
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.36519 | 0.36519 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36519 | 0.38461 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.3689 | 0.36889 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36891 | 0.38461 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.36821 | 0.36821 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36821 | 0.38461 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.3689 | 0.36889 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.36891 | 0.38461 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.3689 | 0.3689 | 0.38461 | 0.38462 | 0.38461 | 0.3846 | 0.3689 | 0.38461 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99999 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.82841 | 0.82752 | 0.83653 | 0.8489 | 0.84805 | 0.84895 | 0.83021 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.51064 | 0.51006 | 0.51555 | 0.50968 | 0.52778 | 0.52304 | 0.51097 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.82871 | 0.82782 | 0.83698 | 0.82645 | 0.85046 | 0.84895 | 0.83068 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.82954 | 0.82866 | 0.83688 | 0.83333 | 0.85738 | 0.84895 | 0.83144 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 1 | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 1 | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## Delta Results
Output spreadsheet for Airside HVAC BESTEST
Aggregator Sheet - DELTA RESULTS for Delta Plots
DELTA 300-400
Pre-Heating Coil Load (QHpreheat) (kWh/h)
Tab Name==> | QAS | DEEAP | DeST | DOE22 | Eplus | IES-VE | TRNSYS | YourData | Blank | Blank | Blank | Blank | Blank
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 - AE401 Heat -29.0/-29.0 | -7.3127 | -7.2782 | -6.73 | -7.0293 | -6.7682 | -6.804 | -7.3112 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 - AE403 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 - AE404 Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 - AE405 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 - AE406 Wet Coil 23.0/20.9 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 - AE426 Wet Coil 23.0/20.9 DB Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 - AE445 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads- Sensible (QCsensible) (kWh/h)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 - AE401 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 - AE403 Dry Coil 15.5/-3.0 | 5.2774 | 5.2419 | 5.0162 | 5.0177 | 5.0777 | 5.084 | 5.278 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 - AE404 Wet Coil 26.9/22.1 | 2.9212 | 2.8821 | 2.6085 | 2.431 | 2.7857 | 2.701 | 2.9287 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 - AE405 Dry Coil 24.9/2.4 No Econo | 5.2806 | 5.2447 | 5.0374 | 4.8149 | 5.1017 | 5.084 | 5.2824 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 - AE406 Wet Coil 23.0/20.9 No Econo | 5.2857 | 5.2594 | 5.0718 | 4.9174 | 5.1602 | 5.085 | 5.2853 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 - AE426 Wet Coil 23.0/20.9 DB Econo | 4.867 | 4.7915 | 4.5396 | 4.5892 | 4.7066 | 4.58 | 4.8855 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 - AE445 Dry Coil 24.9/2.4 Enth. Eco | 5.5454 | 5.5247 | 5.277 | 5.115 | 5.3645 | 5.369 | 5.5625 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads- Latent (QClatent) (kWh/h)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 - AE401 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 - AE403 Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 - AE404 Wet Coil 26.9/22.1 | 0.33412 | 0.32027 | 0.43027 | 0.29717 | 0.30444 | 0.316 | 0.34014 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 - AE405 Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 - AE406 Wet Coil 23.0/20.9 No Econo | 0.85526 | 0.83731 | 1.1349 | 0.939 | 0.90886 | 0.882 | 0.85438 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 - AE426 Wet Coil 23.0/20.9 DB Econo | 7.0651 | 7.0787 | 7.2465 | 6.5238 | 7.1418 | 7.102 | 7.0857 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 - AE445 Dry Coil 24.9/2.4 Enth. Eco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads- Total (QCtotal) (kWh/h)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 - AE401 Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 - AE403 Dry Coil 15.5/-3.0 | 5.2774 | 5.2419 | 5.0162 | 5.0177 | 5.0777 | 5.084 | 5.278 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 - AE404 Wet Coil 26.9/22.1 | 3.2553 | 3.2024 | 3.0388 | 2.7282 | 3.0902 | 3.017 | 3.2689 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 - AE405 Dry Coil 24.9/2.4 No Econo | 5.2806 | 5.2447 | 5.0374 | 4.8149 | 5.1017 | 5.084 | 5.2824 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 - AE406 Wet Coil 23.0/20.9 No Econo | 6.141 | 6.0968 | 6.2066 | 5.8564 | 6.0691 | 5.968 | 6.1397 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 - AE426 Wet Coil 23.0/20.9 DB Econo | 11.9321 | 11.8702 | 11.7862 | 11.113 | 11.8484 | 11.682 | 11.9712 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 - AE445 Dry Coil 24.9/2.4 Enth. Eco | 5.5454 | 5.5247 | 5.277 | 5.115 | 5.3645 | 5.369 | 5.5625 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Economizer 300
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
Total Cooling | 0.32005 | 0.33471 | 0.28782 | 0.35637 | 0.31021 | 0.334 | 0.33386 | 0.33699 | #N/A | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | 0.32005 | 0.33471 | 0.28782 | 0.35637 | 0.31021 | 0.334 | 0.33386 | 0.33699 | #N/A | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Total Cooling | 6.3983 | 6.3814 | 6.1912 | 5.9124 | 6.2871 | 6.251 | 6.4173 | 6.3682 | #N/A | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | -0.46026 | -0.51867 | -0.58455 | -0.36605 | -0.49552 | -0.556 | -0.44441 | -0.56609 | #N/A | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 6.8586 | 6.9001 | 6.7757 | 6.2785 | 6.7827 | 6.808 | 6.8617 | 6.9343 | #N/A | #N/A | #N/A | #N/A | #N/A
Economizer 400
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
Total Cooling | 0.055217 | 0.054705 | 0.048245 | 0.05627 | 0.047365 | 0.049 | 0.053834 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | 0.055217 | 0.054705 | 0.048245 | 0.05627 | 0.047365 | 0.049 | 0.053834 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Total Cooling | 0.60713 | 0.60799 | 0.61163 | 0.65589 | 0.50783 | 0.537 | 0.5858 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | -0.041587 | -0.050749 | -0.052419 | -0.037806 | -0.041867 | -0.051 | -0.044634 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 0.64871 | 0.65874 | 0.66405 | 0.6937 | 0.54969 | 0.588 | 0.63044 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Supply Air W minus System Supply Air W (should be zero)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0% | 6.344e-05% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0% | 0.001287% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0% | 6.344e-05% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0% | 6.344e-05% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0% | 0% | 0% | 0% | 0% | 0% | 1.739% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0% | 0% | 0% | 0% | -0.0002003% | 0% | 0.04436% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0% | 0.006872% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0% | 0% | 0% | 0% | -0.05064% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0% | 0% | 0% | 0% | 0.002223% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Supply Air W minus System Supply Air W ( should be zero)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0% | 6.344e-05% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0% | 0.001287% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0% | 6.344e-05% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0% | 6.344e-05% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0% | 0% | 0% | 0% | -0.0002003% | 0% | 0.04436% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0% | 0.006872% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0% | 0% | 0% | 0% | -0.05064% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0% | 0% | 0% | 0% | 0.002223% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0% | 0% | 0% | 0% | 0% | 0% | 0% | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 delta humidity ratio
Increase in humidity ratio from supply air to zone
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.00064875 | 0.00064878 | 0.00069081 | #N/A | 0.00067657 | 0.000704 | 0.00064486 | 0.00062056 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.00066204 | 0.00066191 | 0.00069436 | #N/A | 0.00067548 | 0.000704 | 0.00066419 | 0.00077097 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.00066666 | 0.00066659 | 0.00069744 | #N/A | 0.00067521 | 0.000704 | 0.00067088 | 0.00069329 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.00066369 | 0.00066359 | 0.00069436 | #N/A | 0.00067548 | 0.000704 | 0.00066584 | 0.00074662 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.00066693 | 0.00066686 | 0.00069842 | #N/A | 0.00067548 | 0.000704 | 0.00066908 | 0.00068798 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.00066693 | 0.00066686 | 0.00069436 | #N/A | 0.00067548 | 0.000704 | 0.00066904 | 0.00069059 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.00066232 | 0.00066221 | 0.00069436 | #N/A | 0.00067548 | 0.000704 | 0.00066443 | 0.00068294 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.0020451 | 0.0020448 | 0.0020724 | #N/A | 0.0020297 | 0.002112 | 0.0020057 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0016795 | 0.001678 | 0.0017081 | #N/A | 0.0016843 | 0.001756 | 0.0016993 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.00089288 | 0.00089161 | 0.00090227 | #N/A | 0.00089367 | 0.000924 | 0.00090036 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0016843 | 0.0016827 | 0.0017062 | #N/A | 0.0016891 | 0.001756 | 0.0017023 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.0016975 | 0.0016958 | 0.001707 | #N/A | 0.0017009 | 0.001756 | 0.0017162 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.0016975 | 0.0016958 | 0.001707 | #N/A | 0.0017009 | 0.001756 | 0.0017152 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0016832 | 0.0016816 | 0.0017062 | #N/A | 0.0016882 | 0.001756 | 0.0017012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 delta humidity ratio
Increase in humidity ratio from supply air to zone
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.00083342 | 0.0008335 | 0.00088697 | #N/A | 0.00086923 | 0.000905 | 0.00082994 | 0.00080882 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.00085051 | 0.00085035 | 0.00089913 | #N/A | 0.00086783 | 0.000905 | 0.00085415 | 0.0009635 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.00085644 | 0.00085641 | 0.00089744 | #N/A | 0.00086748 | 0.000905 | 0.0008619 | 0.00089137 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.00085262 | 0.00085244 | 0.00089913 | #N/A | 0.00086783 | 0.000905 | 0.00085627 | 0.00094198 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.00085679 | 0.00085676 | 0.00089842 | #N/A | 0.00086783 | 0.000905 | 0.00086044 | 0.0008847 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.00085679 | 0.00085676 | 0.00090265 | #N/A | 0.00086783 | 0.000905 | 0.00086039 | 0.00088799 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.00085086 | 0.00085066 | 0.00089913 | #N/A | 0.00086783 | 0.000905 | 0.00085445 | 0.00087815 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.0020512 | 0.002051 | 0.0020696 | #N/A | 0.0020282 | 0.002112 | 0.0020302 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.0017389 | 0.0017367 | 0.001783 | #N/A | 0.0017441 | 0.001819 | 0.00176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.0012267 | 0.0012252 | 0.0012487 | #N/A | 0.0012291 | 0.001271 | 0.0012396 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.0017438 | 0.0017413 | 0.001782 | #N/A | 0.001749 | 0.001819 | 0.001763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.0017575 | 0.0017552 | 0.001781 | #N/A | 0.0017614 | 0.001819 | 0.0017783 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.0017575 | 0.0017552 | 0.001781 | #N/A | 0.0017615 | 0.001819 | 0.0017771 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.0017427 | 0.0017401 | 0.001782 | #N/A | 0.001748 | 0.001819 | 0.0017621 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 1 Latent Gain (gw/s)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.23072 | 0.23076 | 0.23474 | #N/A | 0.23073 | 0.23922 | 0.22932 | 0.22077 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.23034 | 0.23034 | 0.23595 | #N/A | 0.23036 | 0.23922 | 0.23106 | 0.26827 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.23025 | 0.23026 | 0.23699 | #N/A | 0.23026 | 0.23922 | 0.23168 | 0.23444 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.23034 | 0.23035 | 0.23595 | #N/A | 0.23036 | 0.23922 | 0.23106 | 0.25602 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.23034 | 0.23035 | 0.23732 | #N/A | 0.23036 | 0.23922 | 0.23106 | 0.23426 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.23034 | 0.23035 | 0.23595 | #N/A | 0.23036 | 0.23922 | 0.23106 | 0.23434 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.23034 | 0.23035 | 0.23595 | #N/A | 0.23036 | 0.23922 | 0.23106 | 0.23434 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.23072 | 0.23071 | 0.23474 | #N/A | 0.23073 | 0.23923 | 0.22628 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.23034 | 0.23038 | 0.23627 | #N/A | 0.23035 | 0.23924 | 0.23249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.23025 | 0.23022 | 0.23715 | #N/A | 0.23026 | 0.23924 | 0.23217 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.23034 | 0.23035 | 0.23595 | #N/A | 0.23035 | 0.23924 | 0.23217 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.23034 | 0.23034 | 0.23595 | #N/A | 0.23035 | 0.23924 | 0.23235 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.23034 | 0.23034 | 0.23595 | #N/A | 0.23035 | 0.23924 | 0.23216 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.23034 | 0.23035 | 0.23583 | #N/A | 0.23035 | 0.23924 | 0.23216 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone 2 Latent Gain (gw/s)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.34579 | 0.34587 | 0.35162 | #N/A | 0.34583 | 0.35877 | 0.34437 | 0.33571 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.34523 | 0.34524 | 0.35644 | #N/A | 0.34527 | 0.35877 | 0.34672 | 0.39114 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.34509 | 0.34513 | 0.35577 | #N/A | 0.34513 | 0.35877 | 0.34731 | 0.35166 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.34523 | 0.34522 | 0.35644 | #N/A | 0.34527 | 0.35877 | 0.34672 | 0.37684 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.34523 | 0.34527 | 0.35616 | #N/A | 0.34527 | 0.35877 | 0.34672 | 0.35144 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.34523 | 0.34527 | 0.35784 | #N/A | 0.34527 | 0.35877 | 0.34672 | 0.35154 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.34523 | 0.34522 | 0.35644 | #N/A | 0.34527 | 0.35877 | 0.34672 | 0.35154 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.34579 | 0.3458 | 0.35162 | #N/A | 0.34583 | 0.35883 | 0.34226 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.34523 | 0.3453 | 0.35691 | #N/A | 0.34527 | 0.35889 | 0.34873 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.34509 | 0.34509 | 0.35765 | #N/A | 0.34513 | 0.35899 | 0.34827 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.34523 | 0.34522 | 0.35644 | #N/A | 0.34527 | 0.35889 | 0.34827 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.34523 | 0.34525 | 0.35644 | #N/A | 0.34527 | 0.35889 | 0.34853 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.34523 | 0.34525 | 0.35644 | #N/A | 0.34527 | 0.35889 | 0.34827 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.34523 | 0.34522 | 0.35663 | #N/A | 0.34527 | 0.35889 | 0.34827 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Total Zone Latent Gain (gw/s)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | TRNSYS/TESS | OpenSimula/US | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank | Blank/Blank
AE301 Heat -29.0/-29.0 | 0.57651 | 0.57663 | 0.58636 | #N/A | 0.57656 | 0.59799 | 0.57369 | 0.55648 | #N/A | #N/A | #N/A | #N/A | #N/A
AE303 Dry Coil 15.5/-3.0 | 0.57557 | 0.57558 | 0.59239 | #N/A | 0.57563 | 0.59799 | 0.57778 | 0.6594 | #N/A | #N/A | #N/A | #N/A | #N/A
AE304 Wet Coil 26.9/22.1 | 0.57534 | 0.57538 | 0.59276 | #N/A | 0.5754 | 0.59799 | 0.57899 | 0.5861 | #N/A | #N/A | #N/A | #N/A | #N/A
AE305 Dry Coil 24.9/2.4 No Econo | 0.57557 | 0.57557 | 0.59239 | #N/A | 0.57563 | 0.59799 | 0.57778 | 0.63286 | #N/A | #N/A | #N/A | #N/A | #N/A
AE306 Wet Coil 23.0/20.9 No Econo | 0.57557 | 0.57562 | 0.59349 | #N/A | 0.57563 | 0.59799 | 0.57777 | 0.5857 | #N/A | #N/A | #N/A | #N/A | #N/A
AE326 Wet Coil 23.0/20.9 DB Econo | 0.57557 | 0.57562 | 0.59378 | #N/A | 0.57563 | 0.59799 | 0.57777 | 0.58588 | #N/A | #N/A | #N/A | #N/A | #N/A
AE345 Dry Coil 24.9/2.4 Enth. Eco | 0.57557 | 0.57556 | 0.59239 | #N/A | 0.57563 | 0.59799 | 0.57778 | 0.58588 | #N/A | #N/A | #N/A | #N/A | #N/A
AE401 Heat -29.0/-29.0 | 0.57651 | 0.57651 | 0.58636 | #N/A | 0.57655 | 0.59806 | 0.56854 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE403 Dry Coil 15.5/-3.0 | 0.57557 | 0.57568 | 0.59318 | #N/A | 0.57563 | 0.59813 | 0.58122 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE404 Wet Coil 26.9/22.1 | 0.57534 | 0.57532 | 0.5948 | #N/A | 0.57539 | 0.59824 | 0.58044 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE405 Dry Coil 24.9/2.4 No Econo | 0.57557 | 0.57557 | 0.59239 | #N/A | 0.57563 | 0.59813 | 0.58043 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE406 Wet Coil 23.0/20.9 No Econo | 0.57557 | 0.57559 | 0.59239 | #N/A | 0.57563 | 0.59813 | 0.58088 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE426 Wet Coil 23.0/20.9 DB Econo | 0.57557 | 0.57559 | 0.59239 | #N/A | 0.57563 | 0.59813 | 0.58043 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE445 Dry Coil 24.9/2.4 Enth. Eco | 0.57557 | 0.57557 | 0.59246 | #N/A | 0.57563 | 0.59813 | 0.58043 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## QAS
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Quasi-Analytical Solution V2 | [5 empty] | National Renewable Energy Laboratory
1. Use specified units. |  |  |  | Program Version Release Date: |  |  |  | 2014-10-10 |  | Modeler Organization for Tables and Charts (short): |  |  |  | PSU-TAMU-NREL
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | QAS
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2014-11-12 |  | Model / Organization Indentifier for Charts (short): |  |  |  | QAS/PSU-TAMU-NREL
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | Quasi-analytic Solution
| Version: | V2
| Date: | 2014-11-12
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZCsensible) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9307 | 0 | 0.58614 | 8.4195 | 0 | 0 | 0 | 6.3854 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.0034 | 29.3163 | 29.3163 | 29.9222 | 21.1111 | 21.1111
| AE103 | 0 | 1.4654 | 0.58614 | 0 | 0.78348 | 0 | 0.78348 | 32.8432 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016041 | 0.002304 | 0.002304
| AE104 | 0 | 2.9307 | 0.58614 | 0 | 3.4965 | 2.0543 | 5.5508 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9314 | 787.1625 | 859.0555 | 859.0555 | 860.7762 | 836.6895 | 836.6895
[16 empty] | Enthalpy (J/gda) | -28.5404 | 8.0513 | 33.5916 | 33.5916 | 34.2029 | 27.0907 | 27.0907
[16 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32963 | 0.32963 | 0.32963 | 0.32963 | #N/A | 0.21681
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7741 | 20.7741 | 18.5042 | 19.088 | 23.3333 | 23.3333
[16 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043252 | 0.0043252 | 0.0043252 | 0.0043252 | 0.005002 | 0.005002
[16 empty] | Specific volume (L/kgda) | 821.5658 | 838.437 | 838.437 | 831.9622 | 833.6275 | 846.6514 | 846.6514
[16 empty] | Enthalpy (J/gda) | 23.0203 | 31.8833 | 31.8833 | 29.5815 | 30.1736 | 36.2004 | 36.2004
[16 empty] | Mass flow rate (kgda/s) | 0.11149 | 0.34036 | 0.34036 | 0.34036 | 0.34036 | #N/A | 0.22888
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8678 | 24.8678 | 14.9386 | 15.5144 | 23.8889 | 23.8889
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013054 | 0.013054 | 0.010605 | 0.010605 | 0.01128 | 0.01128
[16 empty] | Specific volume (L/kgda) | 872.9245 | 861.9632 | 861.9632 | 830.0307 | 831.6898 | 856.7312 | 856.7312
[16 empty] | Enthalpy (J/gda) | 69.8513 | 58.2685 | 58.2685 | 41.8451 | 42.4358 | 52.7436 | 52.7436
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | #N/A | 0.23098
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZCsensible) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9307 | 0 | 0.58614 | 8.3599 | 0 | 0 | 0 | 6.3854 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.1826 | 29.3163 | 29.3163 | 29.9222 | 21.1111 | 21.1111 | 21.3832
| AE203 | 0 | 1.4654 | 0.58614 | 0 | 0.85614 | 0 | 0.85614 | 32.8432 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016041 | 0.002304 | 0.002304 | 0.002304
| AE204 | 0 | 2.9307 | 0.58614 | 0 | 3.5739 | 2.0543 | 5.6282 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9314 | 787.6715 | 859.0555 | 859.0555 | 860.7762 | 836.6895 | 836.6895 | 837.4631
| AE205 | 0 | 1.4654 | 0.58614 | 0 | 1.9163 | 0 | 1.9163 | 44.5612 | [6 empty] | Enthalpy (J/gda) | -28.5429 | 8.2324 | 33.5942 | 33.5942 | 34.2055 | 27.0925 | 27.0925 | 27.3675
| AE206 | 0 | 1.4654 | 0.58614 | 0 | 1.7064 | 0.97038 | 2.6768 | 100 | [6 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32963 | 0.32963 | 0.32963 | 0.32963 | #N/A | 0.21681 | 0.21681
| AE226 | 0 | 1.4654 | 0.58614 | 0 | 1.5618 | 1.7999 | 3.3617 | 100 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9845 | 20.9845 | 18.5042 | 19.088 | 23.3333 | 23.3333 | 23.6459
| AE245 | 0 | 1.4654 | 0.58614 | 0 | 2.2077 | 0 | 2.2077 | 34.0915 | [6 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043252 | 0.0043252 | 0.0043252 | 0.0043252 | 0.005002 | 0.005002 | 0.005002
[16 empty] | Specific volume (L/kgda) | 821.5658 | 839.0374 | 839.0374 | 831.9622 | 833.6275 | 846.6514 | 846.6514 | 847.5441
[16 empty] | Enthalpy (J/gda) | 23.0217 | 32.0985 | 32.0985 | 29.5832 | 30.1752 | 36.2025 | 36.2025 | 36.5199
[16 empty] | Mass flow rate (kgda/s) | 0.11149 | 0.34036 | 0.34036 | 0.34036 | 0.34036 | #N/A | 0.22888 | 0.22888
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.088 | 25.088 | 14.9386 | 15.5144 | 23.8889 | 23.8889 | 24.215
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013054 | 0.013054 | 0.010605 | 0.010605 | 0.01128 | 0.01128 | 0.01128
[16 empty] | Specific volume (L/kgda) | 872.9245 | 862.5998 | 862.5998 | 830.0307 | 831.6898 | 856.7312 | 856.7312 | 857.6719
[16 empty] | Enthalpy (J/gda) | 69.8537 | 58.4974 | 58.4974 | 41.8464 | 42.4371 | 52.7457 | 52.7457 | 53.0807
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | #N/A | 0.23098 | 0.23098
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0556 | 24.0556 | 18.506 | 19.0896 | 23.3333 | 23.3333 | 23.6458
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0058837 | 0.0058837 | 0.0058837 | 0.0058837 | 0.0065621 | 0.0065621 | 0.0065621
[16 empty] | Specific volume (L/kgda) | 850.4314 | 849.9075 | 849.9075 | 834.0374 | 835.7063 | 848.7583 | 848.7583 | 849.6529
[16 empty] | Enthalpy (J/gda) | 36.4912 | 39.1804 | 39.1804 | 33.5362 | 34.1298 | 40.172 | 40.172 | 40.4903
[16 empty] | Mass flow rate (kgda/s) | 0.11121 | 0.33952 | 0.33952 | 0.33952 | 0.33952 | #N/A | 0.22831 | 0.22831
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4335 | 23.4335 | 18.5142 | 19.0968 | 23.3333 | 23.3333 | 23.6453
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014546 | 0.014546 | 0.013368 | 0.013368 | 0.014054 | 0.014054 | 0.014054
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.8306 | 859.8306 | 844.0036 | 845.6895 | 858.8761 | 858.8761 | 859.7797
[16 empty] | Enthalpy (J/gda) | 62.7099 | 60.5901 | 60.5901 | 52.5203 | 53.121 | 59.2355 | 59.2355 | 59.5574
[16 empty] | Mass flow rate (kgda/s) | 0.1099 | 0.33551 | 0.33551 | 0.33551 | 0.33551 | #N/A | 0.22561 | 0.22561
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5142 | 19.0968 | 23.3333 | 23.3333 | 23.6453
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.013368 | 0.013368 | 0.014054 | 0.014054 | 0.014054
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.9354 | 859.9354 | 844.0036 | 845.6895 | 858.8761 | 858.8761 | 859.7797
[16 empty] | Enthalpy (J/gda) | 62.7099 | 62.7099 | 62.7099 | 52.5203 | 53.121 | 59.2355 | 59.2355 | 59.5574
[16 empty] | Mass flow rate (kgda/s) | 0.33551 | 0.33551 | 0.33551 | 0.33551 | 0.33551 | #N/A | 0.22561 | 0.22561
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5044 | 19.0882 | 23.3333 | 23.3333 | 23.6459
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0051678 | 0.0051678 | 0.0051678
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4314 | 850.4314 | 832.1827 | 833.8485 | 846.8753 | 846.8753 | 847.7683
[16 empty] | Enthalpy (J/gda) | 36.4912 | 36.4912 | 36.4912 | 30.0033 | 30.5955 | 36.6243 | 36.6243 | 36.9419
[16 empty] | Mass flow rate (kgda/s) | 0.34027 | 0.34027 | 0.34027 | 0.34027 | 0.34027 | #N/A | 0.22882 | 0.22882
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Load | Load | Load | Load | Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 2.947 | 0 | 0 | 0 | 24.7331 | 7.7129 | 8.3889 | AE301 | Dry bulb temperature (°C) | -29 | 3.4316 | 7.2222 | 7.2222 | 7.7838 | 29.2787 | 27.8228 | 21.1111 | 22.2222 | 21.6708 | 22.019
| AE303 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 6.7354 | 0 | 6.7354 | 48.1495 | 2.2584 | 2.4572 |  | Humidity ratio (g/gda) | 0.00025893 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0021971 | 0.0023817 | 0.0022901 | 0.0022901
| AE304 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 10.3202 | 6.2583 | 16.5785 | 100 | 0.99332 | 1.519 |  | Specific volume (L/kgda) | 691.9314 | 785.4683 | 796.2333 | 796.2333 | 797.8282 | 858.8717 | 854.7372 | 836.5461 | 839.9533 | 838.262 | 839.252
| AE305 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.3829 | 0 | 9.3829 | 65.719 | 2.2598 | 2.4589 |  | Enthalpy (J/gda) | -28.5429 | 7.3347 | 11.1593 | 11.1593 | 11.726 | 33.4136 | 31.9447 | 26.8208 | 28.4127 | 27.6225 | 27.9743
| AE306 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.9211 | 5.4432 | 14.3643 | 100 | 2.2625 | 2.4624 |  | Mass flow rate (kgda/s) | 0.28139 | 0.77054 | 0.77054 | 0.77054 | 0.77054 | 0.35564 | 0.41491 | #N/A | #N/A | 0.48915 | 0.48915
| AE326 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.4609 | 12.3018 | 20.7626 | 100 | 2.2625 | 2.4624 | AE303 | Dry bulb temperature (°C) | 15.5 | 21.0184 | 21.0184 | 12.2066 | 12.7778 | 19.1796 | 18.7479 | 23.3333 | 24.4444 | 23.8924 | 24.232
| AE345 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.7029 | 0 | 9.7029 | 51.0891 | 2.2587 | 2.4575 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0048927 | 0.0050812 | 0.0049876 | 0.0049876
[16 empty] | Specific volume (L/kgda) | 821.5658 | 839.0074 | 839.0074 | 813.8748 | 815.504 | 833.7629 | 832.5316 | 846.5039 | 849.9317 | 848.2283 | 849.198
[16 empty] | Enthalpy (J/gda) | 23.0217 | 31.8928 | 31.8928 | 22.9579 | 23.5371 | 30.0283 | 29.5906 | 35.9245 | 37.5324 | 36.7334 | 37.0782
[16 empty] | Mass flow rate (kgda/s) | 0.27809 | 0.75384 | 0.75384 | 0.75384 | 0.75384 | 0.34793 | 0.40591 | #N/A | #N/A | 0.47575 | 0.47575
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5732 | 25.5732 | 12.2072 | 12.7778 | 15.5904 | 16.4644 | 23.8889 | 25 | 24.4481 | 24.7899
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.01225 | 0.01225 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0095185 | 0.0097082 | 0.0096139 | 0.0096139
[16 empty] | Specific volume (L/kgda) | 872.9245 | 862.9099 | 862.9099 | 819.8829 | 821.5223 | 829.6035 | 832.1147 | 854.3485 | 857.802 | 856.0862 | 857.0696
[16 empty] | Enthalpy (J/gda) | 69.8537 | 56.9493 | 56.9493 | 34.6208 | 35.2043 | 38.0804 | 38.9741 | 48.2629 | 49.8839 | 49.0785 | 49.4286
[16 empty] | Mass flow rate (kgda/s) | 0.27554 | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.34538 | 0.40294 | #N/A | #N/A | 0.47278 | 0.47278
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4777 | 24.4777 | 12.2068 | 12.7778 | 19.1811 | 18.75 | 23.3333 | 24.4444 | 23.8924 | 24.2318
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0064526 | 0.0066415 | 0.0065476 | 0.0065476
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.9862 | 850.9862 | 815.9007 | 817.5333 | 835.842 | 834.6093 | 848.6104 | 852.0467 | 850.3391 | 851.3109
[16 empty] | Enthalpy (J/gda) | 36.4912 | 39.3684 | 39.3684 | 26.8906 | 27.4712 | 33.9825 | 33.5441 | 39.8934 | 41.5057 | 40.7045 | 41.0501
[16 empty] | Mass flow rate (kgda/s) | 0.2774 | 0.75197 | 0.75197 | 0.75197 | 0.75197 | 0.34706 | 0.40491 | #N/A | #N/A | 0.47457 | 0.47457
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7742 | 23.7742 | 12.2072 | 12.7778 | 19.1841 | 18.7541 | 23.3333 | 24.4444 | 23.8924 | 24.2316
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.011806 | 0.011806 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0095187 | 0.0097086 | 0.0096142 | 0.0096142
[16 empty] | Specific volume (L/kgda) | 859.9354 | 857.1123 | 857.1123 | 819.8829 | 821.5223 | 839.9288 | 838.6933 | 852.751 | 856.2041 | 854.4881 | 855.4639
[16 empty] | Enthalpy (J/gda) | 62.7099 | 53.9677 | 53.9677 | 34.6208 | 35.2043 | 41.7551 | 41.3154 | 47.6948 | 49.3158 | 48.5103 | 48.8576
[16 empty] | Mass flow rate (kgda/s) | 0.27605 | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.34538 | 0.40294 | #N/A | #N/A | 0.47227 | 0.47227
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2072 | 12.7778 | 19.1841 | 18.7541 | 23.3333 | 24.4444 | 23.8924 | 24.2316
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0095187 | 0.0097086 | 0.0096142 | 0.0096142
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.9354 | 859.9354 | 819.8829 | 821.5223 | 839.9288 | 838.6933 | 852.751 | 856.2041 | 854.4881 | 855.4639
[16 empty] | Enthalpy (J/gda) | 62.7099 | 62.7099 | 62.7099 | 34.6208 | 35.2043 | 41.7551 | 41.3154 | 47.6948 | 49.3158 | 48.5103 | 48.8576
[16 empty] | Mass flow rate (kgda/s) | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.34538 | 0.40294 | #N/A | #N/A | 0.47227 | 0.47227
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.2066 | 12.7778 | 19.1799 | 18.7483 | 23.3333 | 24.4444 | 23.8924 | 24.2319
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0051532 | 0.0053417 | 0.005248 | 0.005248
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4314 | 850.4314 | 814.213 | 815.8428 | 834.11 | 832.8785 | 846.8556 | 850.2849 | 848.5808 | 849.5508
[16 empty] | Enthalpy (J/gda) | 36.4912 | 36.4912 | 36.4912 | 23.6145 | 24.194 | 30.6885 | 30.2507 | 36.5871 | 38.1958 | 37.3964 | 37.7413
[16 empty] | Mass flow rate (kgda/s) | 0.75353 | 0.75353 | 0.75353 | 0.75353 | 0.75353 | 0.34778 | 0.40575 | #N/A | #N/A | 0.47555 | 0.47555
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 |  | Zone 1 | Zone 2 |  | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible |  | Latent | Sensible |  | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Load |  | Load | Load |  | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZC1sensible) |  | (QZ1latent) | (QZC2sensible) |  | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) |  | (kWh/h) | (kWh/h) |  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 10.2597 | 0 | 0 | 0 | 4.1447 | 4.4994 | 4.8772 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.2222 | 7.2222 | 7.2968 | 46.92 | 36.0391 | 21.1111 | 22.2222 | #N/A | #N/A
| AE403 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 1.458 | 0 | 1.458 | 36.3949 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.002304 | 0.0023101 | #N/A | #N/A
| AE404 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 7.399 | 5.9242 | 13.3232 | 100 | 0 | 0 |  | Specific volume (L/kgda) | 691.9314 | 691.9314 | 794.5867 | 794.5867 | 794.7981 | 907.0919 | 876.2548 | 836.6895 | 839.8569 | #N/A | #N/A
| AE405 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1023 | 0 | 4.1023 | 53.4629 | 0 | 0 |  | Enthalpy (J/gda) | -28.5429 | -28.5429 | 7.9172 | 7.9172 | 7.9923 | 47.8758 | 36.9234 | 27.0925 | 28.2306 | #N/A | #N/A
| AE406 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6354 | 4.5879 | 8.2233 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28139 | 0.28139 | 0.28139 | 0.28139 | 0.28139 | 0.11281 | 0.16858 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.5938 | 5.2366 | 8.8305 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9553 | 16.9553 | 12.6643 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9495 | 23.9545
| AE445 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1575 | 0 | 4.1575 | 49.575 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0049701 | 0.0050294 | 0.005003 | 0.005003
[16 empty] | Specific volume (L/kgda) | 821.5658 | 826.1765 | 826.1765 | 813.9564 | 814.2796 | 814.2796 | 814.2796 | 846.6083 | 849.8616 | 848.4124 | 848.4267
[16 empty] | Enthalpy (J/gda) | 23.0217 | 25.392 | 25.392 | 21.0486 | 21.1635 | 21.1635 | 21.1635 | 36.1213 | 37.4006 | 36.8307 | 36.8358
[16 empty] | Mass flow rate (kgda/s) | 0.27809 | 0.33569 | 0.33569 | 0.33569 | 0.33569 | 0.13715 | 0.19854 | #N/A | #N/A | 0.057601 | 0.057601
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.7259 | 25.7259 | 12.4805 | 12.7778 | 12.7778 | 12.7778 | 23.8889 | 25 | 24.3792 | 24.4858
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013486 | 0.013486 | 0.0090147 | 0.0090147 | 0.0090147 | 0.0090147 | 0.0099076 | 0.010241 | 0.010055 | 0.010055
[16 empty] | Specific volume (L/kgda) | 872.9245 | 865.0327 | 865.0327 | 820.8802 | 821.7345 | 821.7345 | 821.7345 | 854.875 | 858.5261 | 856.4857 | 856.7924
[16 empty] | Enthalpy (J/gda) | 69.8537 | 60.2554 | 60.2554 | 35.3116 | 35.6156 | 35.6156 | 35.6156 | 49.2534 | 51.2422 | 50.1307 | 50.2399
[16 empty] | Mass flow rate (kgda/s) | 0.27533 | 0.53919 | 0.53919 | 0.53919 | 0.53919 | 0.25787 | 0.28132 | #N/A | #N/A | 0.26386 | 0.26386
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7375 | 24.7375 | 12.6644 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9495 | 23.9544
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0065301 | 0.0065896 | 0.0065631 | 0.0065631
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4494 | 850.4494 | 815.9814 | 816.3051 | 816.3051 | 816.3051 | 848.715 | 851.9764 | 850.5234 | 850.5376
[16 empty] | Enthalpy (J/gda) | 36.4912 | 37.2305 | 37.2305 | 24.975 | 25.0901 | 25.0901 | 25.0901 | 40.0906 | 41.3736 | 40.802 | 40.807
[16 empty] | Mass flow rate (kgda/s) | 0.2774 | 0.33473 | 0.33473 | 0.33473 | 0.33473 | 0.13676 | 0.19797 | #N/A | #N/A | 0.057335 | 0.057335
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1615 | 23.1615 | 12.6647 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9492 | 23.9541
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014755 | 0.014755 | 0.009126 | 0.009126 | 0.009126 | 0.009126 | 0.010823 | 0.010883 | 0.010857 | 0.010857
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.3233 | 859.3233 | 821.5545 | 821.8794 | 821.8794 | 821.8794 | 854.5129 | 857.7967 | 856.333 | 856.3471
[16 empty] | Enthalpy (J/gda) | 62.7099 | 60.8393 | 60.8393 | 35.7809 | 35.8965 | 35.8965 | 35.8965 | 51.0146 | 52.3077 | 51.7313 | 51.7363
[16 empty] | Mass flow rate (kgda/s) | 0.27552 | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.13569 | 0.19643 | #N/A | #N/A | 0.056614 | 0.056614
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6647 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9492 | 23.9541
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.009126 | 0.009126 | 0.009126 | 0.009126 | 0.010823 | 0.010883 | 0.010857 | 0.010857
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.9354 | 859.9354 | 821.5545 | 821.8794 | 821.8794 | 821.8794 | 854.5129 | 857.7967 | 856.333 | 856.3471
[16 empty] | Enthalpy (J/gda) | 62.7099 | 62.7099 | 62.7099 | 35.7809 | 35.8965 | 35.8965 | 35.8965 | 51.0146 | 52.3077 | 51.7313 | 51.7363
[16 empty] | Mass flow rate (kgda/s) | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.13569 | 0.19643 | #N/A | #N/A | 0.056614 | 0.056614
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6644 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9495 | 23.9544
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0061741 | 0.0062336 | 0.0062071 | 0.0062071
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4314 | 850.4314 | 815.5192 | 815.8428 | 815.8428 | 815.8428 | 848.2342 | 851.4937 | 850.0416 | 850.0558
[16 empty] | Enthalpy (J/gda) | 36.4912 | 36.4912 | 36.4912 | 24.0789 | 24.194 | 24.194 | 24.194 | 39.1847 | 40.4668 | 39.8956 | 39.9007
[16 empty] | Mass flow rate (kgda/s) | 0.33495 | 0.33495 | 0.33495 | 0.33495 | 0.33495 | 0.13685 | 0.1981 | #N/A | #N/A | 0.057395 | 0.057395
* n/a = not applicable

## DEEAP
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | AAON Detailed Energy and Economic Analysis Program 1.1.2 | [5 empty] | AAON Inc.
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | AAON
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | DEEAP
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2012-12-10 |  | Model / Organization Indentifier for Charts (short): |  |  |  | DEEAP/AAON
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | G latent gains updated slightly
Version:
Date:
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9309 |  | 0.58608 | 8.4133 | 0 | 0 | 0 | 6.3813 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.0029 | 29.3262 | 29.3262 | 29.9328 | 21.1111
| AE103 |  | 1.4649 | 0.586 | 0 | 0.78407 | 0 | 0.78407 | 32.5417 | [6 empty] | Humidity ratio (g/gda) | 0.00025894 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016042 | 0.0023041
| AE104 |  | 2.9303 | 0.58608 | 0 | 3.4882 | 2.0648 | 5.553 | 99.9992 | [6 empty] | Specific volume (L/kgda) | 691.8414 | 787.0586 | 858.9719 | 858.9719 | 860.6945 | 836.5805
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11283 | 0.32966 | 0.32966 | 0.32966 | 0.32966 | #N/A
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7741 | 20.7741 | 18.5 | 19.0845 | 23.3333
[16 empty] | Humidity ratio (g/gda) | 0.0028954 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049611
[16 empty] | Specific volume (L/kgda) | 821.4055 | 838.2732 | 838.2732 | 831.7876 | 833.4546 | 846.4857
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11151 | 0.34043 | 0.34043 | 0.34043 | 0.34043 | #N/A
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.8889 | 24.8642 | 24.8642 | 14.9302 | 15.5066 | 23.8889
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.013053 | 0.013053 | 0.0106 | 0.010599 | 0.011274
[16 empty] | Specific volume (L/kgda) | 872.7897 | 861.8387 | 861.8387 | 829.891 | 831.5517 | 856.6119
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11019 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | #N/A
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9309 |  | 0.58608 | 8.3488 | 0 | 0 | 0 | 6.3813 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.1972 | 29.3262 | 29.3262 | 29.9328 | 21.1111 | 21.1111 | 21.4061
| AE203 |  | 1.4649 | 0.586 | 0 | 0.85303 | 0 | 0.85303 | 32.5417 | [6 empty] | Humidity ratio (g/gda) | 0.00025894 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0023041 | 0.0023041 | 0.0023041
| AE204 |  | 2.9303 | 0.58608 | 0 | 3.5587 | 2.0648 | 5.6234 | 99.9992 | [6 empty] | Specific volume (L/kgda) | 691.8414 | 787.6103 | 858.9719 | 858.9719 | 860.6945 | 836.5805 | 836.5805 | 837.4192
| AE205 |  | 1.4642 | 0.58608 | 0 | 1.9099 | 0 | 1.9099 | 44.3101 | [6 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE206 |  | 1.4644 | 0.58608 | 0 | 1.7005 | 0.9632 | 2.6637 | 99.9992 | [6 empty] | Mass flow rate (kgda/s) | 0.11283 | 0.32966 | 0.32966 | 0.32966 | 0.32966 | #N/A | 0.21683 | 0.21683
| AE226 |  | 1.4644 | 0.58608 | 0 | 1.5568 | 1.7782 | 3.335 | 99.9992 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9741 | 20.9741 | 18.5 | 19.0845 | 23.3333 | 23.3333 | 23.6304
| AE245 |  | 1.4642 | 0.58608 | 0 | 2.202 | 0 | 2.202 | 33.8389 | [6 empty] | Humidity ratio (g/gda) | 0.0028954 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042845 | 0.0049611 | 0.0049611 | 0.0049611
[16 empty] | Specific volume (L/kgda) | 821.4055 | 838.8436 | 838.8436 | 831.7876 | 833.4546 | 846.4857 | 846.4857 | 847.3338
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11151 | 0.34043 | 0.34043 | 0.34043 | 0.34043 | #N/A | 0.22893 | 0.22893
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.8889 | 25.0648 | 25.0648 | 14.9302 | 15.5066 | 23.8889 | 23.8889 | 24.186
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.013053 | 0.013053 | 0.0106 | 0.0106 | 0.011274 | 0.011274 | 0.011274
[16 empty] | Specific volume (L/kgda) | 872.7897 | 862.4186 | 862.4186 | 829.891 | 831.5517 | 856.6119 | 856.6119 | 857.4688
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11019 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | #N/A | 0.23102 | 0.23102
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.8889 | 24.0415 | 24.0415 | 18.5041 | 19.0883 | 23.3333 | 23.3333 | 23.6303
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0058499 | 0.0058499 | 0.0058499 | 0.00585 | 0.0065284 | 0.0065284 | 0.0065284
[16 empty] | Specific volume (L/kgda) | 850.243 | 849.7105 | 849.7105 | 833.8783 | 835.549 | 848.6018 | 848.6018 | 849.4517
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11123 | 0.33958 | 0.33958 | 0.33958 | 0.33958 | #N/A | 0.22835 | 0.22835
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4231 | 23.4231 | 18.5118 | 19.0951 | 23.3333 | 23.3333 | 23.6297
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.014534 | 0.014534 | 0.013367 | 0.013367 | 0.014053 | 0.014053 | 0.014053
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.6718 | 859.6718 | 843.8842 | 845.5719 | 858.7617 | 858.7617 | 859.6202
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10991 | 0.33555 | 0.33555 | 0.33555 | 0.33555 | #N/A | 0.22564 | 0.22564
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5118 | 19.0951 | 23.3333 | 23.3333 | 23.6297
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.015523 | 0.015523 | 0.013367 | 0.013367 | 0.014053 | 0.014053 | 0.014053
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.778 | 859.778 | 843.8842 | 845.5719 | 858.7617 | 858.7617 | 859.6202
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33555 | 0.33555 | 0.33555 | 0.33555 | 0.33555 | #N/A | 0.22564 | 0.22564
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 18.5025 | 19.0888 | 23.3333 | 23.3333 | 23.6304
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.005134 | 0.005134 | 0.005134
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.243 | 850.243 | 832.0238 | 833.6965 | 846.7192 | 846.7192 | 847.5674
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.34033 | 0.34033 | 0.34033 | 0.34033 | 0.34033 | #N/A | 0.22886 | 0.22886
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9309 |  | 0.58608 | 2.3449 |  | 0.87918 | 2.9697 | 0 | 0 | 0 | 24.7328 | 7.7075 | 8.3822 | AE301 | Dry bulb temperature (°C) | -29 | 3.3982 | 7.2222 | 7.2222 | 7.7845 | 29.2883 | 27.8298 | 21.1111 | 22.2222 | 21.6708 | 21.9663
| AE303 |  | 1.4649 | 0.586 |  | 2.3449 | 0.87904 | 0 | 6.7082 | 0 | 6.7082 | 47.6873 | 2.2547 | 2.4515 |  | Humidity ratio (g/gda) | 0.00025894 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0021972 | 0.0023819 | 0.0022902 | 0.0022902
| AE304 |  | 2.9309 | 0.58608 |  | 3.5169 | 0.87918 | 0 | 10.2556 | 6.2947 | 16.5503 | 99.9992 | 0.98884 | 1.5135 |  | Specific volume (L/kgda) | 691.8414 | 785.2713 | 796.1298 | 796.1298 | 797.7263 | 858.7874 | 854.646 | 836.4373 | 839.8441 | 838.1531 | 838.9934
| AE305 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 9.3496 | 0 | 9.3496 | 65.3364 | 2.2561 | 2.4532 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE306 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 8.8688 | 5.4441 | 14.3129 | 99.9992 | 2.2588 | 2.4568 |  | Mass flow rate (kgda/s) | 0.28143 | 0.77064 | 0.77064 | 0.77064 | 0.77064 | 0.35568 | 0.41496 | #N/A | #N/A | 0.48921 | 0.48921
| AE326 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 8.3501 | 12.3442 | 20.6943 | 99.9992 | 2.2588 | 2.4568 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.9919 | 20.9919 | 12.2059 | 12.7778 | 19.1761 | 18.7408 | 23.3333 | 24.4444 | 23.8924 | 24.19
| AE345 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 9.6843 | 0 | 9.6843 | 50.7067 | 2.255 | 2.4518 |  | Humidity ratio (g/gda) | 0.0028954 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0048518 | 0.0050403 | 0.0049466 | 0.0049466
[16 empty] | Specific volume (L/kgda) | 821.4055 | 838.7678 | 838.7678 | 813.7138 | 815.3446 | 833.59 | 832.3485 | 846.3382 | 849.7654 | 848.0623 | 848.912
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27814 | 0.75399 | 0.75399 | 0.75399 | 0.75399 | 0.348 | 0.40599 | #N/A | #N/A | 0.47585 | 0.47585
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.8889 | 25.5414 | 25.5414 | 12.2065 | 12.7778 | 15.5808 | 16.4551 | 23.8889 | 25 | 24.4481 | 24.7459
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.012254 | 0.012254 | 0.008852 | 0.008852 | 0.008852 | 0.008852 | 0.0095186 | 0.0097084 | 0.0096141 | 0.0096141
[16 empty] | Specific volume (L/kgda) | 872.7897 | 862.7095 | 862.7095 | 819.774 | 821.4151 | 829.4677 | 831.9792 | 854.2369 | 857.69 | 855.9744 | 856.831
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27557 | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.34542 | 0.40299 | #N/A | #N/A | 0.47284 | 0.47284
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.8889 | 24.4471 | 24.4471 | 12.2061 | 12.7778 | 19.1778 | 18.7428 | 23.3333 | 24.4444 | 23.8924 | 24.1899
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0064187 | 0.0066076 | 0.0065137 | 0.0065137
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.7417 | 850.7417 | 815.7483 | 817.3825 | 835.6783 | 834.4349 | 848.4538 | 851.8894 | 850.1822 | 851.0336
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27745 | 0.75211 | 0.75211 | 0.75211 | 0.75211 | 0.34713 | 0.40498 | #N/A | #N/A | 0.47466 | 0.47466
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7478 | 23.7478 | 12.2065 | 12.7778 | 19.1807 | 18.747 | 23.3333 | 24.4444 | 23.8924 | 24.1897
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.011794 | 0.011794 | 0.008852 | 0.008852 | 0.008852 | 0.008852 | 0.0095189 | 0.0097087 | 0.0096144 | 0.0096144
[16 empty] | Specific volume (L/kgda) | 859.778 | 856.9076 | 856.9076 | 819.774 | 821.4151 | 839.8095 | 839.8095 | 852.6395 | 856.0923 | 854.3765 | 855.2315
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27609 | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.34542 | 0.40299 | #N/A | #N/A | 0.47233 | 0.47233
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2065 | 12.7778 | 19.1807 | 18.747 | 23.3333 | 24.4444 | 23.8924 | 24.1897
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.015523 | 0.015523 | 0.008852 | 0.008852 | 0.008852 | 0.008852 | 0.0095189 | 0.0097087 | 0.0096144 | 0.0096144
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.778 | 859.778 | 819.774 | 821.4151 | 839.8095 | 838.5636 | 852.6395 | 856.0923 | 854.3765 | 855.2315
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.34542 | 0.40299 | #N/A | #N/A | 0.47233 | 0.47233
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.2059 | 12.7778 | 19.1765 | 18.7411 | 23.3333 | 24.4444 | 23.8924 | 24.19
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0051194 | 0.0053078 | 0.0052142 | 0.0052142
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.243 | 850.243 | 814.0611 | 815.6925 | 833.9468 | 832.7047 | 846.6994 | 850.1279 | 848.4242 | 849.2742
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.75367 | 0.75367 | 0.75367 | 0.75367 | 0.75367 | 0.34785 | 0.40582 | #N/A | #N/A | 0.47566 | 0.47566
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9309 |  | 0.58608 | 2.3448 |  | 0.87918 | 10.2479 | 0 | 0 | 0 | 4.1474 | 4.4963 | 4.8725 | AE401 | Dry bulb temperature (°C) | -29 | -28.9957 | 7.2222 | 7.2222 | 7.3083 | 46.9483 | 36.0548 | 21.1111 | 22.2222 | #N/A | #N/A | Aug 7, 2015: Blank entries replaced with "NA" by JN
| AE403 |  | 1.4649 | 0.586 |  | 2.3449 | 0.87904 | 0 | 1.4663 | 0 | 1.4663 | 36.0086 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025894 | 0.00025911 | 0.00025911 | 0.00025911 | 0.00025861 | 0.00025861 | 0.00025861 | 0.0023034 | 0.0023096 | #N/A | #N/A | Makes output as blank rather than "0", as participant intended.
| AE404 |  | 2.9309 | 0.58608 |  | 3.5169 | 0.87918 | 0 | 7.3735 | 5.9745 | 13.348 | 99.9992 | 0 | 0 |  | Specific volume (L/kgda) | 691.8414 | 691.8536 | 794.4835 | 794.4835 | 794.7275 | 907.0536 | 876.1849 | 836.5796 | 839.7468 | #N/A | #N/A
| AE405 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 4.1049 | 0 | 4.1049 | 53.1717 | 0 | 0 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE406 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 3.6094 | 4.6068 | 8.2162 | 99.9992 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28143 | 0.28143 | 0.28143 | 0.28143 | 0.28143 | 0.11283 | 0.1686 | #N/A | #N/A | 0 | 0
| AE426 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 3.5586 | 5.2655 | 8.8241 | 99.9992 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9621 | 16.9621 | 12.6466 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9504 | 23.981
| AE445 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 4.1596 | 0 | 4.1596 | 49.2421 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0028954 | 0.0032519 | 0.0032519 | 0.0032519 | 0.0032519 | 0.0032519 | 0.0032519 | 0.00493 | 0.0049886 | 0.0049625 | 0.0049625
[16 empty] | Specific volume (L/kgda) | 821.4055 | 826.0373 | 826.0373 | 813.7497 | 814.1232 | 814.1236 | 814.1236 | 846.4437 | 849.6953 | 848.2496 | 848.3367
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27814 | 0.33612 | 0.33612 | 0.33612 | 0.33612 | 0.13729 | 0.19883 | #N/A | #N/A | 0.057974 | 0.057974
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.8889 | 25.91 | 25.91 | 12.4612 | 12.7778 | 12.7777 | 12.7777 | 23.8889 | 25 | 24.3794 | 24.4935
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.01348 | 0.01348 | 0.0090036 | 0.0090036 | 0.0090036 | 0.0090036 | 0.0098953 | 0.010229 | 0.010042 | 0.010042
[16 empty] | Specific volume (L/kgda) | 872.7897 | 864.9025 | 864.9025 | 820.7028 | 821.6126 | 821.6122 | 821.6122 | 854.7464 | 858.3966 | 856.3573 | 856.6857
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27537 | 0.53988 | 0.53988 | 0.53988 | 0.53988 | 0.25821 | 0.28167 | #N/A | #N/A | 0.2645 | 0.2645
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.8889 | 24.728 | 24.728 | 12.6468 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9504 | 23.9573
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.004814 | 0.004814 | 0.004814 | 0.004814 | 0.0048143 | 0.0048143 | 0.006497 | 0.0065555 | 0.0065295 | 0.0065295
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.268 | 850.268 | 815.7831 | 816.1571 | 816.1574 | 816.1574 | 848.5594 | 851.8189 | 850.3696 | 850.3892
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27745 | 0.33516 | 0.33516 | 0.33516 | 0.33516 | 0.13689 | 0.19826 | #N/A | #N/A | 0.057705 | 0.057705
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1628 | 23.1628 | 12.6472 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9501 | 23.9568
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.014721 | 0.014721 | 0.0091159 | 0.0091159 | 0.0091159 | 0.0091159 | 0.010812 | 0.010871 | 0.010845 | 0.010845
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.169 | 859.169 | 821.3834 | 821.7587 | 821.7585 | 821.7585 | 854.3852 | 857.6675 | 856.2071 | 856.2265
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27556 | 0.33253 | 0.33253 | 0.33253 | 0.33253 | 0.13583 | 0.19671 | #N/A | #N/A | 0.056975 | 0.056975
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6472 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9501 | 23.9568
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.015523 | 0.015523 | 0.0091159 | 0.0091159 | 0.0091159 | 0.0091159 | 0.010812 | 0.010871 | 0.010845 | 0.010845
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.778 | 859.778 | 821.3834 | 821.7587 | 821.7585 | 821.7585 | 854.3852 | 857.6675 | 856.2071 | 856.2265
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33253 | 0.33253 | 0.33253 | 0.33253 | 0.33253 | 0.13583 | 0.19671 | #N/A | #N/A | 0.056975 | 0.056975
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.6519 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9504 | 23.9573
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0061387 | 0.0061973 | 0.0061712 | 0.0061712
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.243 | 850.243 | 815.3186 | 815.6925 | 815.6925 | 815.6925 | 848.0757 | 851.3333 | 849.8849 | 849.9045
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33538 | 0.33538 | 0.33538 | 0.33538 | 0.33538 | 0.13698 | 0.19839 | #N/A | #N/A | 0.057768 | 0.057768
* n/a = not applicable

## DeST
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air System Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Designer's Simulation Toolkit 2 | [5 empty] | Tsinghua University / Lawarence Berkeley National Laboratory
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | TsinghuaU-LBNL
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | DeST
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2013-11-21 |  | Model / Organization Indentifier for Charts (short): |  |  |  | DeST/TsinghuaU-LBNL
| C50..C52: | Software Name, Version, and Date of Results
| C61..J63: | Coil Loads, Fan Coil Air System, Cases AE101 - AE104
| S61..Y75: | Detailed Outputs, Fan Coil Air System, Cases AE101-AE104
| C89..J95: | Coil Loads, Single Zone Air System, Cases AE201 - AE245
| S89..Z123: | Detailed Outputs, Single Zone Air System, Cases AE201-AE245
| C137..O143: | Coil Loads, Constant Volume Terminal Reheat Air System, Cases AE301 - AE345
| S137..AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, Cases AE301-AE345
| C185..O191: | Coil Loads, Variable Air Volume Air System, Cases AE401 - AE445
| S185..AC219: | Detailed Outputs, Variable Air Volume Air System, Cases AE401-AE445
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
Software:
Version:
Date:
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.93 |  | 0.5867 | 8.4521 | 0 | 0 | 0 | [6 empty] | AET101a | Dry bulb temperature (°C) | -29 | 4.4073 | 29.0892 | 29.0892 | 29.6791 | 21.0991 | 21.0991
| AE103 |  | 1.4666 | 0.58971 | 0 | 0.7777 | 0 | 0.7777 | 33.03 | [6 empty] | Humidity ratio (g/gda) | 0.00026 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0023324 | 0.0023324
| AE104 |  | 2.9311 | 0.58578 | 0 | 3.5428 | 2.293 | 5.8358 | 98.66 | [6 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | -28.5113 | 8.55 | 33.4266 | 33.4266 | 34.02 | 27.1262 | 27.1262
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
[15 empty] | AET103a | Dry bulb temperature (°C) | 15.5 | 20.722 | 20.722 | 18.4621 | 19.052 | 23.3479 | 23.3479
[16 empty] | Humidity ratio (g/gda) | 0.002948 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0050311 | 0.0050311
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 31.83 | 31.83 | 29.54 | 30.14 | 36.26 | 36.26
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
[15 empty] | AET104a | Dry bulb temperature (°C) | 26.9 | 24.8861 | 24.8861 | 14.7013 | 15.2912 | 23.8764 | 23.8764
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.012947 | 0.012947 | 0.010296 | 0.010296 | 0.010986 | 0.010986
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 57.97 | 57.97 | 40.79 | 41.4 | 51.94 | 51.94
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.93 |  | 0.59 | 8.3847 | 0 | 0 | 0 | [6 empty] | AET201a | Dry bulb temperature (°C) | -29 | 4.604 | 29.0892 | 29.0892 | 29.6791 | 21.099 | 21.099 | 21.3939
| AE203 |  | 1.4666 | 0.58971 | 0 | 0.84533 | 0 | 0.84533 | 33.03 | [6 empty] | Humidity ratio (g/gda) | 0.00026 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0023324 | 0.0023324 | 0.0023324
| AE204 |  | 2.9311 | 0.58578 | 0 | 3.6078 | 2.2888 | 5.8966 | 98.62 | [6 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
| AE205 |  | 1.47 | 0.59 | 0 | 1.9287 | 0 | 1.9287 | 44.81 | [6 empty] | Enthalpy (J/gda) | -28.5113 | 8.75 | 33.43 | 33.43 | 34.02 | 27.13 | 27.13 | 27.42
| AE206 |  | 1.47 | 0.59 | 0 | 1.7314 | 1.0866 | 2.8181 | 99.36 | [6 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
| AE226 |  | 1.4655 | 0.58971 | 0 | 1.593 | 2.0498 | 3.6428 | 99.65 | [5 empty] | AET203a | Dry bulb temperature (°C) | 15.5 | 20.9187 | 20.9187 | 18.4622 | 19.0521 | 23.3481 | 23.3481 | 23.643
| AE245 |  | 1.4663 | 0.58971 | 0 | 2.2158 | 0 | 2.2158 | 34.33 | [6 empty] | Humidity ratio (g/gda) | 0.002948 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0050311 | 0.0050311 | 0.0050311
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 32.02 | 32.02 | 29.54 | 30.14 | 36.26 | 36.26 | 36.56
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET204a | Dry bulb temperature (°C) | 26.9 | 25.0935 | 25.0935 | 14.7219 | 15.3118 | 23.897 | 23.897 | 24.192
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.012952 | 0.012952 | 0.010306 | 0.010306 | 0.010995 | 0.010995 | 0.011319
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 58.2 | 58.2 | 40.84 | 41.44 | 51.99 | 51.99 | 52.29
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET205a | Dry bulb temperature (°C) | 24.9 | 24.052 | 24.052 | 18.4632 | 19.0531 | 23.3479 | 23.3479 | 23.6428
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.0058987 | 0.0058987 | 0.0058987 | 0.0059 | 0.0065931 | 0.0065931 | 0.00659
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5 | 39.18 | 39.18 | 33.5 | 34.1 | 40.23 | 40.23 | 40.53
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET206a | Dry bulb temperature (°C) | 23 | 23.4067 | 23.4067 | 18.4552 | 19.0451 | 23.3378 | 23.3378 | 23.6328
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.014484 | 0.014484 | 0.013227 | 0.013227 | 0.013921 | 0.013921 | 0.013921
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 60.36 | 60.36 | 52.06 | 52.67 | 58.85 | 58.85 | 59.16
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET226a | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.4446 | 19.0345 | 23.3272 | 23.3272 | 23.6221
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.01563 | 0.01563 | 0.013257 | 0.013257 | 0.013951 | 0.013951 | 0.013951
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 62.8515 | 62.8515 | 52.13 | 52.74 | 58.92 | 58.92 | 58.92
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET245a | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.4632 | 19.0531 | 23.3479 | 23.3479 | 23.6429
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.0052044 | 0.0052044 | 0.0052044
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.51 | 36.51 | 36.51 | 29.98 | 30.58 | 36.7 | 36.7 | 36.7
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.93 |  | 0.59 | 2.35 |  | 0.88 | 3.58 | 0 | 0 | 0 |  | 7.4721 | 8.0774 | AET301 | Dry bulb temperature (°C) | -29 | 2.3874 | 7.22 | 7.22 | 7.8099 | 29.6699 | 28.084 | 21.111 | 22.222 | 21.7092 | 22.0042
| AE303 |  | 1.4666 | 0.58971 |  | 2.3459 | 0.89087 | 0 | 6.4595 | 0 | 6.4595 | 48.22 | 2.1363 | 2.3 |  | Humidity ratio (g/gda) | 0.00026 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0022251 | 0.0024213 | 0.0023308 | 0.0023308
| AE304 |  | 2.9337 | 0.59273 |  | 3.5165 | 0.89389 | 0 | 10.0587 | 7.0108 | 17.0695 | 95.49 | 0.85904 | 1.3509 |  | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
| AE305 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 9.1806 | 0 | 9.1806 | 65.84 | 2.1367 | 2.3017 |  | Enthalpy (J/gda) | -28.5113 | 6.24 | 11.11 | 11.11 | 11.71 | 33.74 | 32.14 | 26.8658 | 28.4854 | 27.74 | 28.04
| AE306 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 8.6987 | 6.1035 | 14.8022 | 96.21 | 2.1374 | 2.3004 |  | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
| AE326 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 8.1141 | 12.8792 | 20.9933 | 98.89 | 2.1374 | 2.3005 | AET303 | Dry bulb temperature (°C) | 15.5 | 20.87 | 20.87 | 12.2049 | 12.7948 | 19.05 | 18.57 | 23.333 | 24.444 | 23.9462 | 24.2412
| AE345 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 9.4684 | 0 | 9.4684 | 51.33 | 2.1374 | 2.3005 |  | Humidity ratio (g/gda) | 0.002948 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0049298 | 0.0051345 | 0.00504 | 0.0049864
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 31.73 | 31.73 | 22.95 | 23.55 | 29.88 | 29.4 | 35.99 | 37.63 | 36.89 | 37.19
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET304 | Dry bulb temperature (°C) | 26.9 | 25.5957 | 25.5957 | 12.2047 | 12.7946 | 15.3101 | 16.1852 | 23.889 | 25 | 24.502 | 24.7969
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.012182 | 0.012182 | 0.0084426 | 0.0084426 | 0.0084426 | 0.0084426 | 0.00914 | 0.00934 | 0.0092505 | 0.0092505
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 56.75 | 56.75 | 33.56 | 34.16 | 36.73 | 37.62 | 47.2602 | 48.9046 | 48.17 | 48.47
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET305 | Dry bulb temperature (°C) | 24.9 | 24.4854 | 24.4854 | 12.2049 | 12.7948 | 19.0515 | 18.572 | 23.333 | 24.444 | 23.9462 | 24.2412
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0064918 | 0.0066965 | 0.006602 | 0.006602
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 39.36 | 39.36 | 26.89 | 27.49 | 33.84 | 33.36 | 39.96 | 41.61 | 40.86 | 41.16
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET306 | Dry bulb temperature (°C) | 23 | 23.7552 | 23.7552 | 12.1759 | 12.7658 | 19.0246 | 18.5398 | 23.333 | 24.444 | 23.9171 | 24.2121
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.011752 | 0.011752 | 0.0084916 | 0.0084916 | 0.0084916 | 0.0084916 | 0.00919 | 0.00939 | 0.0092962 | 0.009673
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 53.77 | 53.77 | 33.66 | 34.26 | 40.65 | 40.15 | 46.81 | 48.47 | 47.69 | 47.99
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2038 | 12.7937 | 19.0525 | 18.5677 | 23.333 | 24.444 | 23.9451 | 24.24
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.01563 | 0.01563 | 0.0087474 | 0.0087474 | 0.0087474 | 0.0087474 | 0.0094417 | 0.00965 | 0.009552 | 0.009552
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 62.8515 | 62.8515 | 34.33 | 34.93 | 41.32 | 40.8278 | 47.45 | 49.14 | 48.37 | 48.37
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.2049 | 12.7948 | 19.0515 | 18.572 | 23.333 | 24.444 | 23.9462 | 24.2412
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.0052044 | 0.0054091 | 0.0053146 | 0.0053146
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 36.5061 | 36.5061 | 23.64 | 24.24 | 30.55 | 30.07 | 36.68 | 38.33 | 37.59 | 37.59
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.93 |  | 0.59 | 2.35 |  | 0.88 | 10.31 | 0 | 0 | 0 |  | 4.5019 | 4.891 | AET401 | Dry bulb temperature (°C) | -29 | -29 | 7.22 | 7.22 | 7.3073 | 46.8548 | 35.9521 | 21.111 | 22.222 | #N/A | #N/A | Aug 7, 2015: Entries replaced with "NA" by JN
| AE403 |  | 1.4666 | 0.58971 |  | 2.3459 | 0.89087 | 0 | 1.4433 | 0 | 1.4433 | 36.39 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.0023324 | 0.0023296 | #N/A | #N/A | Air property output not appropriate for 0 RA mass flow.
| AE404 |  | 2.9337 | 0.59273 |  | 3.5165 | 0.89389 | 0 | 7.4502 | 6.5805 | 14.0307 | 97.24 | 0 | 0 |  | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | #N/A | #N/A
| AE405 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 4.1432 | 0 | 4.1432 | 53.52 | 0 | 0 |  | Enthalpy (J/gda) | -28.5113 | -28.5113 | 7.91 | 7.91 | 8 | 47.76 | 36.8 | 27.1382 | 28.2525 | #N/A | #N/A
| AE406 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 3.6269 | 4.9686 | 8.5955 | 99.38 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.11327 | 0.1699 | #N/A | #N/A | 0 | 0
| AE426 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 3.5745 | 5.6327 | 9.2072 | 99.58 | 0 | 0 | AET403 | Dry bulb temperature (°C) | 15.5 | 16.888 | 16.888 | 12.6699 | 12.795 | 12.795 | 12.795 | 23.333 | 24.444 | 24.005 | 24.0094
| AE445 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 4.1914 | 0 | 4.1914 | 49.78 | 0 | 0 |  | Humidity ratio (g/gda) | 0.002948 | 0.00329 | 0.00329 | 0.00329 | 0.0032876 | 0.0032876 | 0.0032876 | 0.0049958 | 0.0050706 | 0.00504 | 0.00504
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 25.3 | 25.3 | 21.03 | 21.16 | 21.16 | 21.16 | 36.1476 | 37.47 | 36.95 | 36.95
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.3385 | 0.3385 | 0.3385 | 0.3385 | 0.13832 | 0.20018 | #N/A | #N/A | 0.055336 | 0.055336
[15 empty] | AET404 | Dry bulb temperature (°C) | 26.9 | 25.7508 | 25.7508 | 12.4633 | 12.7916 | 12.7916 | 12.7916 | 23.889 | 25 | 24.48 | 24.5817
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.013454 | 0.013454 | 0.0087492 | 0.0087492 | 0.0087492 | 0.0087492 | 0.0096515 | 0.0099979 | 0.0098321 | 0.0098321
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 60.15 | 60.15 | 34.6 | 34.93 | 34.93 | 34.93 | 48.56 | 50.58 | 49.63 | 49.73
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.54925 | 0.54925 | 0.54925 | 0.54925 | 0.26284 | 0.28641 | #N/A | #N/A | 0.26609 | 0.26609
[15 empty] | AET405 | Dry bulb temperature (°C) | 24.9 | 24.7517 | 24.7517 | 12.6704 | 12.795 | 12.795 | 12.795 | 23.333 | 24.444 | 23.9959 | 24.0003
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.004851 | 0.004851 | 0.004851 | 0.004851 | 0.004851 | 0.004851 | 0.0065572 | 0.006633 | 0.0065986 | 0.0065986
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 37.2162 | 37.2162 | 24.97 | 25.1 | 25.1 | 25.1 | 40.1156 | 41.45 | 40.92 | 40.92
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.13829 | 0.20003 | #N/A | #N/A | 0.055153 | 0.055153
[15 empty] | AET406 | Dry bulb temperature (°C) | 23 | 23.1638 | 23.1638 | 12.6693 | 12.7939 | 12.7939 | 12.7939 | 23.333 | 24.444 | 24.0041 | 24.0085
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.014845 | 0.014845 | 0.0090684 | 0.0090684 | 0.0090684 | 0.0090684 | 0.010775 | 0.010849 | 0.010819 | 0.010819
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 61.03 | 61.03 | 35.62 | 35.74 | 35.74 | 35.74 | 50.85 | 52.18 | 51.65 | 51.65
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33835 | 0.33835 | 0.33835 | 0.33835 | 0.13822 | 0.20014 | #N/A | #N/A | 0.055191 | 0.055191
[15 empty] | AET426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6574 | 12.782 | 12.782 | 12.782 | 23.333 | 24.444 | 23.9922 | 23.9966
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.01563 | 0.01563 | 0.0090802 | 0.0090802 | 0.0090802 | 0.0090802 | 0.010787 | 0.010861 | 0.010831 | 0.010831
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 62.8515 | 62.8515 | 35.63 | 35.76 | 35.76 | 35.76 | 50.88 | 52.2078 | 51.67 | 51.67
[16 empty] | Mass flow rate (kgda/s) | 0.33835 | 0.33835 | 0.33835 | 0.33835 | 0.33835 | 0.13822 | 0.20014 | #N/A | #N/A | 0.055153 | 0.055153
[15 empty] | AET445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6704 | 12.795 | 12.795 | 12.795 | 23.333 | 24.444 | 24.0049 | 24.0093
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.0062162 | 0.006292 | 0.006261 | 0.006261
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 36.5061 | 36.5061 | 24.11 | 24.24 | 24.24 | 24.24 | 39.26 | 40.58 | 40.05 | 40.06
[16 empty] | Mass flow rate (kgda/s) | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.13822 | 0.20014 | #N/A | #N/A | 0.055153 | 0.055153
* n/a = not applicable

## DOE22
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | DOE-2.2 V48L | [5 empty] | National Renewable Energy Laboratory
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | NREL
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | DOE-2.2
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2015-03-12 |  | Model / Organization Indentifier for Charts (short): |  |  |  | DOE-2.2/NREL
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | DOE2.2 Design Day
| Version: | 2.2-48L
| Date: | 2015-03-12
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone |  | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible |  | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Load |  | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZsensible) |  | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh) |  | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9307 | 0 | 0.58614 | 8.7675 | 0 | 0 | 0 | 6.4033 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.3889 | 29.2222 | 29.2222 | 29.2222 | 21.1111 | 21.1111
| AE103 | 0 | 1.4654 | 0.58614 | 0 | 0.77693 | 0 | 0.77693 | 31.6536 | [6 empty] | Humidity ratio (g/gda) | 0.0003 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0022 | 0.0022
| AE104 | 0 | 2.9307 | 0.58614 | 0 | 3.521 | 2.0119 | 5.5329 | 99.9615 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11954 | 0.35862 | 0.35862 | 0.35862 | 0.35862 | 0.35862 | 0.23908
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.6889 | 21.2778 | 19 | 19 | 23.3333
[16 empty] | Humidity ratio (g/gda) | 0.0029 | 0.0043 | 0.0043 | 0.0043 | 0.0043 | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11241 | 0.33724 | 0.33724 | 0.33724 | 0.33724 | 0.33724 | 0.22483
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.8889 | 24.9056 | 25.5 | 15.2222 | 15.2222 | 23.8889 | 23.8889
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.0132 | 0.0132 | 0.0108 | 0.0108 | 0.0115 | 0.0115
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10928 | 0.32785 | 0.32785 | 0.32785 | 0.32785 | 0.32785 | 0.21857
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9307 | 0 | 0.58614 | 8.7092 | 0 | 0 | 0 | 6.6125 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6111 | 28.6667 | 28.6667 | #N/A | 21.1111 | 21.1111 | 21.3889
| AE203 | 0 | 1.4654 | 0.58614 | 0 | 0.84024 | 0 | 0.84024 | 32.7731 | [6 empty] | Humidity ratio (g/gda) | 0.0003 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0022 | 0.0022 | 0.0022
| AE204 | 0 | 2.9307 | 0.58614 | 0 | 3.5901 | 2.1212 | 5.7114 | 100 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE205 | 0 | 1.4654 | 0.58614 | 0 | 1.9085 | 0 | 1.9085 | 44.8531 | [6 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE206 | 0 | 1.4654 | 0.58614 | 0 | 1.7233 | 1.0082 | 2.7314 | 99.9317 | [6 empty] | Mass flow rate (kgda/s) | 0.1197 | 0.35909 | 0.35909 | 0.35909 | 0.35909 | 0.35909 | 0.2394 | 0.2394
| AE226 | 0 | 1.4654 | 0.58614 | 0 | 1.5972 | 1.8077 | 3.4049 | 99.9317 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.8889 | 20.8889 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6111
| AE245 | 0 | 1.4654 | 0.58614 | 0 | 2.1878 | 0 | 2.1878 | 34.2864 | [6 empty] | Humidity ratio (g/gda) | 0.0029 | 0.0043 | 0.0043 | 0.0043 | 0.0043 | 0.005 | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11256 | 0.33768 | 0.33768 | 0.33768 | 0.33768 | 0.33768 | 0.22512 | 0.22512
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.8889 | 25.1111 | 25.1111 | 14.6111 | #N/A | 23.8889 | 23.8889 | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.013 | 0.013 | 0.0104 | 0.0104 | 0.0111 | 0.0111 | 0.0111
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10948 | 0.32843 | 0.32843 | 0.32843 | 0.32843 | 0.32843 | 0.21895 | 0.21895
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.8889 | 24.0556 | 24.0556 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0059 | 0.0059 | 0.0059 | 0.0059 | 0.0066 | 0.0066 | 0.0066
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11109 | 0.33327 | 0.33327 | 0.33327 | 0.33327 | 0.33327 | 0.22218 | 0.22218
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4444 | 23.4444 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6111
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0145 | 0.0145 | 0.0133 | 0.0133 | 0.014 | 0.014 | 0.014
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10983 | 0.32948 | 0.32948 | 0.32948 | 0.32948 | 0.32948 | 0.21965 | 0.21965
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6667
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0156 | 0.0156 | 0.0133 | 0.0133 | 0.0141 | 0.0141 | 0.0141
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.21961 | 0.21961
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0052 | 0.0052 | 0.0052
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33309 | 0.33309 | 0.33309 | 0.33309 | 0.33309 | 0.33309 | 0.22206 | 0.22206
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | -2.9307 | 0 | 0.58614 | -2.3446 | 0 | 0.87921 | 3.7882 | 0 | 0 | 0 | 23.9613 | 7.706 | 8.3763 | AE301 | Dry bulb temperature (°C) | -29 | #N/A | 7.2222 | 7.2222 | 7.7778 | #N/A | #N/A | 21.1111 | 22.2222 | #N/A | 21.9444
| AE303 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 6.4197 | 0 | 6.4197 | 47.9247 | 2.15 | 2.3194 |  | Humidity ratio (g/gda) | 0.0003 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | #N/A | #N/A | 0.0022 | 0.0022
| AE304 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 9.8897 | 6.214 | 16.1037 | 100 | 0.79774 | 1.2681 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE305 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.9287 | 0 | 8.9287 | 65.5319 | 2.0723 | 2.2232 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE306 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.5975 | 5.4338 | 14.0314 | 100 | 2.1107 | 2.2695 |  | Mass flow rate (kgda/s) | 0.29649 | 0.77088 | 0.77088 | 0.77088 | 0.77088 | 0.35579 | 0.41509 | #N/A | #N/A | 0.47438 | 0.47438
| AE326 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.2315 | 11.7123 | 19.9438 | 100 | 2.1256 | 2.2886 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8333 | 20.8333 | 12.1667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.2222
| AE345 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.2851 | 0 | 9.2851 | 51.1359 | 2.0887 | 2.2414 |  | Humidity ratio (g/gda) | 0.0029 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | #N/A | #N/A | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28151 | 0.73193 | 0.73193 | 0.73193 | 0.73193 | 0.33781 | 0.39412 | #N/A | #N/A | 0.45042 | 0.45042
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.8889 | 25.5556 | 25.5556 | 12.2222 | 12.8333 | #N/A | #N/A | 23.8889 | 25 | #N/A | 24.7222
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.0124 | 0.0124 | 0.0089 | 0.0089 | 0.0089 | 0.0089 | #N/A | #N/A | 0.0097 | 0.0097
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.2735 | 0.71109 | 0.71109 | 0.71109 | 0.71109 | 0.32819 | 0.38289 | #N/A | #N/A | 0.43759 | 0.43759
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.8889 | 24.4444 | 24.4444 | 12.2778 | 12.8889 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | #N/A | #N/A | 0.0066 | 0.0066
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27741 | 0.72126 | 0.72126 | 0.72126 | 0.72126 | 0.33289 | 0.38837 | #N/A | #N/A | 0.44385 | 0.44385
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7222 | 23.7222 | 12.2222 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.012 | 0.012 | 0.0089 | 0.0089 | 0.0089 | 0.0089 | #N/A | #N/A | 0.0097 | 0.0097
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27538 | 0.716 | 0.716 | 0.716 | 0.716 | 0.33046 | 0.38554 | n/a* | n/a* | 0.44061 | 0.44061
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2222 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0156 | 0.0156 | 0.0089 | 0.0089 | 0.0089 | 0.0089 | #N/A | #N/A | 0.0097 | 0.0097
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.71372 | 0.71372 | 0.71372 | 0.71372 | 0.71372 | 0.32941 | 0.38431 | #N/A | #N/A | 0.43921 | 0.43921
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.2222 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | #N/A | #N/A | 0.0053 | 0.0053
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.72169 | 0.72169 | 0.72169 | 0.72169 | 0.72169 | 0.33309 | 0.3886 | #N/A | #N/A | 0.44412 | 0.44412
* =na()
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo) | Sep 6, 2015: AE401 Tma deleted per email with M. Kennedy of Sep 3, 2015.
| AE401 | -2.9307 | 0 | 0.58614 | -2.3446 | 0 | 0.87921 | 10.8176 | 0 | 0 | 0 | 4.8015 | 4.5839 | 5.0147 | AE401 | Dry bulb temperature (°C) | -29 | #N/A | 7.2222 | 7.2222 | 7.2778 | #N/A | #N/A | 21.1111 | 22.2222 | #N/A | #N/A | #N/A
| AE403 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 1.4021 | 0 | 1.4021 | 34.2896 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | #N/A | #N/A | #N/A | #N/A
| AE404 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 7.4587 | 5.9168 | 13.3755 | 100 | 0 | 0 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE405 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1138 | 0 | 4.1138 | 51.8548 | 0 | 0 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE406 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6801 | 4.4948 | 8.1749 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.29707 | 0.29707 | 0.29707 | 0.29707 | 0.29707 | 0.11883 | 0.17824 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6423 | 5.1885 | 8.8308 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7778 | 16.7778 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | 7.6667
| AE445 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1701 | 0 | 4.1701 | 49.664 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | #N/A | #N/A | 0.0041 | 0.0041
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28597 | 0.33688 | 0.33688 | 0.33688 | 0.33688 | 0.13784 | 0.19904 | #N/A | #N/A | 0.050903 | 0.050903
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.8889 | 25.7222 | 25.7222 | 12.4444 | 12.7778 | #N/A | #N/A | 23.8889 | 25 | #N/A | 24.5 | -0.72222
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.0135 | 0.0135 | 0.009 | 0.009 | 0.009 | 0.009 | #N/A | #N/A | 0.0101 | 0.0101
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27289 | 0.53541 | 0.53541 | 0.53541 | 0.53541 | 0.25542 | 0.27998 | #N/A | #N/A | 0.26252 | 0.26252
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.8889 | 24.7222 | 24.7222 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | -0.27778
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | #N/A | #N/A | 0.0059 | 0.0059
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27761 | 0.33591 | 0.33591 | 0.33591 | 0.33591 | 0.13714 | 0.19877 | #N/A | #N/A | 0.058299 | 0.058299
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1667 | 23.1667 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | 1.2778
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0147 | 0.0147 | 0.0092 | 0.0092 | 0.0092 | 0.0092 | #N/A | #N/A | 0.0103 | 0.0103
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27474 | 0.32968 | 0.32968 | 0.32968 | 0.32968 | 0.13462 | 0.19506 | #N/A | #N/A | 0.054947 | 0.054947
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | 1.4444
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0156 | 0.0156 | 0.0092 | 0.0092 | 0.0092 | 0.0092 | #N/A | #N/A | 0.0104 | 0.0104
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.13451 | 0.1949 | #N/A | #N/A | 0.054902 | 0.054902
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | -0.44444
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | #N/A | #N/A | 0.0057 | 0.0057
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33586 | 0.33586 | 0.33586 | 0.33586 | 0.33586 | 0.13712 | 0.19874 | #N/A | #N/A | 0.05829 | 0.05829
* =na()

## Eplus
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air System Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | EnergyPlus 8.2.0 | [5 empty] | GARD Analytics
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | GARD
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | EnergyPlus
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2015-01-14 |  | Model / Organization Indentifier for Charts (short): |  |  |  | EnergyPlus/GARD
| C50..C52: | Software Name, Version, and Date of Results
| C61..J63: | Coil Loads, Fan Coil Air System, Cases AE101 - AE104
| S61..Y75: | Detailed Outputs, Fan Coil Air System, Cases AE101-AE104
| C89..J95: | Coil Loads, Single Zone Air System, Cases AE201 - AE245
| S89..Z123: | Detailed Outputs, Single Zone Air System, Cases AE201-AE245
| C137..O143: | Coil Loads, Constant Volume Terminal Reheat Air System, Cases AE301 - AE345
| S137..AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, Cases AE301-AE345
| C185..O191: | Coil Loads, Variable Air Volume Air System, Cases AE401 - AE445
| S185..AC219: | Detailed Outputs, Variable Air Volume Air System, Cases AE401-AE445
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | EnergyPlus
| Version: | 8.2.0
| Date: | 1/14/2015 w/ post proc correction 20Aug2015, see Q130
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | -2.931 |  | 0.5861 | 8.4534 | 0 | 0 | 0 | 6.5151 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4539 | 29.0494 | 29.0494 | 29.6355 | 21.1183 | 21.1183
| AE103 |  | 1.465 | 0.5861 | 0 | 0.76554 | 0 | 0.76554 | 32.5142 | [6 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0022887 | 0.0022887
| AE104 |  | 2.931 | 0.5861 | 0 | 3.4986 | 2.1742 | 5.6728 | 99.6158 | [6 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | -28.5066 | 8.5207 | 33.309 | 33.309 | 33.8997 | 27.0344 | 27.0344
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.726 | 20.726 | 18.5095 | 19.0928 | 23.3293 | 23.3293
[16 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049599 | 0.0049599
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.7063 | 31.7063 | 29.4615 | 30.0522 | 36.0616 | 36.0616
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8949 | 24.8949 | 14.9265 | 15.5032 | 23.8823 | 23.8823
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013079 | 0.013079 | 0.010558 | 0.010558 | 0.011233 | 0.011233
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 58.3316 | 58.3316 | 41.6971 | 42.2878 | 52.5907 | 52.5907
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | -2.931 |  | 0.5861 | 8.387 | 8.048e-08 | 1.8383e-05 | 1.8464e-05 | 6.5149 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6476 | 29.0498 | 29.0498 | 29.6359 | 21.1187 | 21.1187 | 21.4084
| AE203 |  | 1.465 | 0.5861 | 0 | 0.83269 | 0 | 0.83269 | 32.5148 | [6 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0022887 | 0.0022887 | 0.0022887
| AE204 |  | 2.931 | 0.5861 | 0 | 3.5657 | 2.1735 | 5.7392 | 99.6397 | [6 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
| AE205 |  | 1.465 | 0.5861 | 0 | 1.9127 | 0 | 1.9127 | 44.111 | [6 empty] | Enthalpy (J/gda) | -28.5066 | 8.7159 | 33.3094 | 33.3094 | 33.9001 | 27.0348 | 27.0348 | 27.3272
| AE206 |  | 1.465 | 0.5861 | 0 | 1.6967 | 1.0417 | 2.7383 | 99.0255 | [6 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
| AE226 |  | 1.465 | 0.5861 | 0 | 1.5548 | 1.8634 | 3.4182 | 99.8073 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9201 | 20.9201 | 18.5093 | 19.0925 | 23.3288 | 23.3288 | 23.6201
| AE245 |  | 1.465 | 0.5861 | 0 | 2.2073 | 0 | 2.2073 | 33.9915 | [6 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049599 | 0.0049599 | 0.0049599
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.9029 | 31.9029 | 29.4612 | 30.0519 | 36.0611 | 36.0611 | 36.3565
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.0862 | 25.0862 | 14.9264 | 15.5031 | 23.8822 | 23.8822 | 24.1702
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013081 | 0.013081 | 0.010561 | 0.010561 | 0.011236 | 0.011236 | 0.011236
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 58.5327 | 58.5327 | 41.7033 | 42.2941 | 52.5969 | 52.5969 | 52.8923
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0456 | 24.0456 | 18.5236 | 19.1052 | 23.3296 | 23.3296 | 23.62
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.005832 | 0.005832 | 0.005832 | 0.005832 | 0.0065075 | 0.0065075 | 0.0065075
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 39.0081 | 39.0081 | 33.3995 | 33.9902 | 39.9994 | 39.9994 | 40.2948
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4106 | 23.4106 | 18.5888 | 19.1626 | 23.33 | 23.33 | 23.6165
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.014507 | 0.014507 | 0.013302 | 0.013302 | 0.013978 | 0.013978 | 0.013978
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 60.4363 | 60.4363 | 52.4066 | 52.9973 | 59.0066 | 59.0066 | 59.302
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5897 | 19.1634 | 23.33 | 23.33 | 23.6164
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.015565 | 0.015565 | 0.01341 | 0.01341 | 0.014086 | 0.014086 | 0.014086
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 62.7048 | 62.7048 | 52.6815 | 53.2723 | 59.2816 | 59.2816 | 59.5769
[16 empty] | Mass flow rate (kgda/s) | 0.34102 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5115 | 19.0946 | 23.3294 | 23.3294 | 23.6205
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051565 | 0.0051565 | 0.0051565
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 36.4346 | 36.4346 | 29.962 | 30.5528 | 36.562 | 36.562 | 36.8573
[16 empty] | Mass flow rate (kgda/s) | 0.34102 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
* n/a = not applicable
Note: Aug 2015 - Preheat Coil Outlet Temp was linked to wrong output variable, i.e. Preheat Coil Outlet Setpoint Temp. Link corrected.
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | -2.931 |  | 0.5861 | -2.345 |  | 0.8792 | 3.5747 | 0 | 0 | 0 | 23.8906 | 7.5057 | 8.1309 | AE301 | Dry bulb temperature (°C) | -29 | 2.4185 | 7.22 | 7.22 | 7.8063 | 29.649 | 28.0886 | 21.1299 | 22.2485 | 21.6893 | 21.982
| AE303 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 6.4764 | 0 | 6.4764 | 47.4569 | 2.1827 | 2.3607 |  | Humidity ratio (g/gda) | 0.00025901 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0021723 | 0.0023649 | 0.0022686 | 0.0022686
| AE304 |  | 2.931 | 0.5861 |  | 3.517 | 0.8792 | 0 | 10.1563 | 6.6217 | 16.778 | 99.1258 | 0.94208 | 1.4552 |  | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
| AE305 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 9.1994 | 0 | 9.1994 | 64.909 | 2.193 | 2.3739 |  | Enthalpy (J/gda) | -28.5066 | 6.1776 | 11.0156 | 11.0156 | 11.6064 | 33.6155 | 32.0433 | 26.7502 | 28.3684 | 27.5593 | 27.8547
| AE306 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 8.7437 | 5.7489 | 14.4926 | 99.2475 | 2.2136 | 2.4005 |  | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
| AE326 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 8.2481 | 12.5316 | 20.7797 | 99.9275 | 2.2141 | 2.4012 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8531 | 20.8531 | 12.197 | 12.7804 | 19.1013 | 18.6401 | 23.3385 | 24.4517 | 23.8952 | 24.1865
| AE345 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 9.5096 | 0 | 9.5096 | 50.9944 | 2.1849 | 2.3635 |  | Humidity ratio (g/gda) | 0.0029334 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0048436 | 0.0050359 | 0.0049397 | 0.0049397
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.5397 | 31.5397 | 22.7746 | 23.3653 | 29.7658 | 29.2989 | 35.775 | 37.3934 | 36.5842 | 36.8796
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5756 | 25.5756 | 12.2012 | 12.7797 | 15.485 | 16.3615 | 23.8914 | 25.0047 | 24.4481 | 24.737
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012324 | 0.012324 | 0.0087725 | 0.0087725 | 0.0087725 | 0.0087725 | 0.0094477 | 0.00964 | 0.0095439 | 0.0095439
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 57.1062 | 57.1062 | 34.3988 | 34.9895 | 37.752 | 38.6471 | 48.0548 | 49.6829 | 48.8688 | 49.1642
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4598 | 24.4598 | 12.1989 | 12.7806 | 19.1133 | 18.6566 | 23.3385 | 24.4517 | 23.8952 | 24.1857
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0063912 | 0.0065835 | 0.0064873 | 0.0064873
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 39.1326 | 39.1326 | 26.6821 | 27.2729 | 33.7034 | 33.2397 | 39.7127 | 41.3343 | 40.5235 | 40.8188
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7256 | 23.7256 | 12.2019 | 12.7804 | 19.1369 | 18.6889 | 23.3385 | 24.4517 | 23.8952 | 24.1841
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.011867 | 0.011867 | 0.0087839 | 0.0087839 | 0.0087839 | 0.0087839 | 0.0094593 | 0.0096517 | 0.0095555 | 0.0095555
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 54.0424 | 54.0424 | 34.4281 | 35.0189 | 41.5099 | 41.0525 | 47.5192 | 49.1471 | 48.3331 | 48.6285
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2017 | 12.7801 | 19.1373 | 18.6896 | 23.3385 | 24.4517 | 23.8952 | 24.184
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.015565 | 0.015565 | 0.0088448 | 0.0088448 | 0.0088448 | 0.0088448 | 0.0095202 | 0.0097126 | 0.0096164 | 0.0096164
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 62.7048 | 62.7048 | 34.5816 | 35.1723 | 41.6648 | 41.2075 | 47.6741 | 49.3022 | 48.4881 | 48.7835
[16 empty] | Mass flow rate (kgda/s) | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.197 | 12.78 | 19.1037 | 18.6434 | 23.3385 | 24.4517 | 23.8952 | 24.1863
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051565 | 0.0053488 | 0.0052527 | 0.0052527
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 36.4346 | 36.4346 | 23.5643 | 24.155 | 30.562 | 30.0957 | 36.5712 | 38.1903 | 37.3807 | 37.6761
[16 empty] | Mass flow rate (kgda/s) | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
* n/a = not applicable
Note: Aug 2015 - Preheat Coil Outlet Temp was linked to wrong output variable, i.e. Preheat Coil Outlet Setpoint Temp. Link corrected.
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | -2.931 |  | 0.5861 | -2.345 |  | 0.8792 | 10.343 | 0 | 0 | 0 | 4.1501 | 4.5034 | 4.9022 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.2031 | 7.2031 | 7.2901 | 46.6969 | 35.8886 | 21.1452 | 22.2593 | #N/A | #N/A | Aug 21, 2015: Entries replaced with "NA" by JN
| AE403 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 1.3987 | 0 | 1.3987 | 35.8492 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.0022887 | 0.0022872 | #N/A | #N/A | Air property output not appropriate for 0 RA mass flow.
| AE404 |  | 2.931 | 0.5861 |  | 3.517 | 0.8792 | 0 | 7.3706 | 6.3173 | 13.6879 | 98.7059 | 0 | 0 |  | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | #DIV/0! | #DIV/0! | #N/A | #N/A
| AE405 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 4.0977 | 0 | 4.0977 | 52.7786 | 0 | 0 |  | Enthalpy (J/gda) | -28.5066 | -28.5066 | 7.8892 | 7.8892 | 7.9766 | 47.5931 | 36.7273 | 27.0614 | 28.1819 | #N/A | #N/A
| AE406 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 3.5834 | 4.84 | 8.4235 | 99.7649 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28418 | 0.28418 | 0.28418 | 0.28418 | 0.28418 | 0.11367 | 0.17051 | n/a* | n/a* | 0 | 0
| AE426 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 3.5416 | 5.3897 | 8.9313 | 99.9528 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7888 | 16.7888 | 12.6598 | 12.78 | 12.78 | 12.78 | 23.3441 | 24.4608 | 23.9508 | 23.9546
| AE445 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 4.1451 | 0 | 4.1451 | 49.4632 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029334 | 0.003241 | 0.003241 | 0.003241 | 0.003241 | 0.003241 | 0.003241 | 0.0049254 | 0.0049851 | 0.0049578 | 0.0049578
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 25.0767 | 25.0767 | 20.9029 | 21.0244 | 21.0244 | 21.0244 | 35.9889 | 37.2733 | 36.6866 | 36.6905
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.13676 | 0.19796 | n/a* | n/a* | 0.050546 | 0.050919
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.7623 | 25.7623 | 12.4725 | 12.7797 | 12.7808 | 12.7808 | 23.9001 | 25.0168 | 24.3846 | 24.4749
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013543 | 0.013543 | 0.0088944 | 0.0088944 | 0.0088944 | 0.0088944 | 0.009788 | 0.010124 | 0.0099335 | 0.0099335
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 60.4045 | 60.4045 | 34.9834 | 35.2972 | 35.2982 | 35.2982 | 48.93 | 50.9269 | 49.7961 | 49.8885
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.53845 | 0.53845 | 0.53845 | 0.53845 | 0.25766 | 0.28079 | n/a* | n/a* | 0.25427 | 0.25427
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.758 | 24.758 | 12.661 | 12.7802 | 12.7802 | 12.7802 | 23.3441 | 24.4607 | 23.9497 | 23.9534
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0064728 | 0.0065327 | 0.0065053 | 0.0065053
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 37.0618 | 37.0618 | 24.7987 | 24.9195 | 24.9195 | 24.9195 | 39.9261 | 41.2141 | 40.6246 | 40.6284
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.33415 | 0.33415 | 0.33415 | 0.33415 | 0.13638 | 0.19741 | n/a* | n/a* | 0.049606 | 0.049969
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1345 | 23.1345 | 12.6637 | 12.78 | 12.7899 | 12.7899 | 23.3441 | 24.4607 | 23.9468 | 23.95
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.014891 | 0.014891 | 0.0091064 | 0.0091064 | 0.0091018 | 0.0091018 | 0.010803 | 0.010863 | 0.010835 | 0.010835
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 61.1277 | 61.1277 | 35.7139 | 35.8327 | 35.8312 | 35.8312 | 50.9427 | 52.2412 | 51.6436 | 51.6468
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.33145 | 0.33145 | 0.33145 | 0.33145 | 0.13543 | 0.19602 | n/a* | n/a* | 0.047271 | 0.047271
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6638 | 12.7801 | 12.79 | 12.79 | 23.3441 | 24.4607 | 23.9468 | 23.9499
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.015565 | 0.015565 | 0.0091238 | 0.0091238 | 0.009124 | 0.009124 | 0.010825 | 0.010885 | 0.010858 | 0.010858
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 62.7048 | 62.7048 | 35.758 | 35.8769 | 35.8875 | 35.8875 | 50.9995 | 52.2981 | 51.7004 | 51.7036
[16 empty] | Mass flow rate (kgda/s) | 0.33144 | 0.33144 | 0.33144 | 0.33144 | 0.33144 | 0.13543 | 0.19601 | n/a* | n/a* | 0.047261 | 0.047261
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6608 | 12.7802 | 12.7802 | 12.7802 | 23.3441 | 24.4607 | 23.9499 | 23.9536
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0061691 | 0.006229 | 0.0062016 | 0.0062016
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 36.4346 | 36.4346 | 24.0343 | 24.1552 | 24.1552 | 24.1552 | 39.1535 | 40.4408 | 39.8519 | 39.8557
[16 empty] | Mass flow rate (kgda/s) | 0.33427 | 0.33427 | 0.33427 | 0.33427 | 0.33427 | 0.13645 | 0.19752 | n/a* | n/a* | 0.049791 | 0.050091
* n/a = not applicable
EnergyPlus 4-Pipe Fan Coil
| Last Hour of Simulation - Summary Outputs - Fan Coil Air System | [13 empty] | EnergyPlus 4-Pipe Fan Coil
|  | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZsensible) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AET101a | -2.931 | 0.5861 | 8.4527 | 0 | 0 | 0 | 29.9418 | [6 empty] | AET101a | Dry bulb temperature (°C) | -29 | 4.4496 | 29.6291 | 5.0358 | 29.6291 | 21.1119 | 21.1119
| AET103a | 1.465 | 0.5861 | 0 | 0.76509 | 0 | 0.76509 | 31.3427 | [7 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0022888 | 0.0022888
| AET104a | 2.931 | 0.5861 | 0 | 3.4965 | 2.1082 | 5.6047 | 98.0115 | [7 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | -28.5066 | 8.5164 | 33.8933 | 9.1072 | 33.8933 | 27.0279 | 27.0279
| Notes: | [14 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
| 1) EnergyPlus 4-Pipe Fan Coil model only allows a blow-through configuration with the heating coil placed after the cooling coil | [13 empty] | AET103a | Dry bulb temperature (°C) | 15.5 | 20.7283 | 19.0965 | 19.0965 | 19.0965 | 23.3328 | 23.3328
| 2) Outdoor air and exhaust air interchange takes place automatically within the fan coil unit without the aid of an exhaust fan | [14 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049598 | 0.0049598
| and therefore the fan coil return air flow rate is always equal to the supply air flow rate | [14 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.7087 | 30.0559 | 30.0559 | 30.0559 | 36.0651 | 36.0651
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
[15 empty] | AET104a | Dry bulb temperature (°C) | 26.9 | 24.8985 | 15.5126 | 15.5126 | 15.5126 | 23.8882 | 23.8882
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013235 | 0.010791 | 0.010791 | 0.010791 | 0.011466 | 0.011466
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 58.7307 | 42.8864 | 42.8864 | 42.8864 | 53.1892 | 53.1892
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
* n/a = not applicable

## IES-VE
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Integrated Environmental Solutions Virtual Environment IES-VE 2014.2 | [5 empty] | Integrated Environmental Solutions
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | IES
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | IES-VE
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2015-02-20 |  | Model / Organization Indentifier for Charts (short): |  |  |  | IES-VE/IES
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | IES-VE
| Version: | <VE>2014.2
| Date: | 2015-02-20
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.931 | 0 | 0.5861 | 8.513 | 0 | 0 | 0 | 6.75 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4073 | 28.994 | 28.994 | 29.5758 | 21.111 | 21.111
| AE103 | 0 | 1.465 | 0.5861 | 0 | 0.762 | 0 | 0.762 | 32.91 | [6 empty] | Humidity ratio (g/gda) | 0.000262 | 0.00167 | 0.00167 | 0.00167 | 0.00167 | 0.00237 | 0.002374
| AE104 | 0 | 2.931 | 0.5861 | 0 | 3.48 | 2.127 | 5.607 | 100 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7214 | 20.7214 | 18.5195 | 19.1013 | 23.3321 | 23.3321
[16 empty] | Humidity ratio (g/gda) | 0.002947 | 0.004355 | 0.004355 | 0.004355 | 0.004355 | 0.005059 | 0.005059
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8934 | 24.8934 | 14.8437 | 15.4255 | 23.8901 | 23.8901
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.013136 | 0.013136 | 0.010581 | 0.010581 | 0.011285 | 0.011285
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.931 | 0 | 0.5861 | 8.446 | 0 | 0 | 0 | 6.75 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6011 | 28.9937 | 28.9937 | 29.5755 | 21.1107 | 21.1107 | 21.4016
| AE203 | 0 | 1.465 | 0.5861 | 0 | 0.83 | 0 | 0.83 | 32.91 | [6 empty] | Humidity ratio (g/gda) | 0.000262 | 0.00167 | 0.00167 | 0.00167 | 0.00167 | 0.002374 | 0.002374 | 0.002374
| AE204 | 0 | 2.931 | 0.5861 | 0 | 3.547 | 2.128 | 5.675 | 100 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE205 | 0 | 1.465 | 0.5861 | 0 | 1.915 | 0 | 1.915 | 44.59 | [6 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE206 | 0 | 1.465 | 0.5861 | 0 | 1.695 | 1 | 2.696 | 100 | [6 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
| AE226 | 0 | 1.465 | 0.5861 | 0 | 1.552 | 1.825 | 3.377 | 100 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9148 | 20.9148 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
| AE245 | 0 | 1.564 | 0.5861 | 0 | 2.21 | 0 | 2.21 | 34.06 | [6 empty] | Humidity ratio (g/gda) | 0.002947 | 0.004355 | 0.004355 | 0.004355 | 0.004355 | 0.005059 | 0.005059 | 0.005059
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.0861 | 25.0861 | 14.8418 | 15.4236 | 23.8882 | 23.8882 | 24.1791
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.013135 | 0.013135 | 0.01058 | 0.01058 | 0.011284 | 0.011284 | 0.011284
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0481 | 24.0481 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.005916 | 0.005916 | 0.005916 | 0.005916 | 0.00662 | 0.00662 | 0.00662
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4148 | 23.4148 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.014624 | 0.014624 | 0.013424 | 0.013424 | 0.014128 | 0.014128 | 0.014128
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.015616 | 0.015616 | 0.013424 | 0.013424 | 0.014128 | 0.014128 | 0.014128
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.005212 | 0.005212 | 0.005212
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.22654 | 0.22654
* n/a = not applicable
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 3.647 | 0 | 0 | 0 | 24.65 | 7.539 | 8.17 | AE301 | Dry bulb temperature (°C) | -29 | 2.3582 | 7.22 | 7.22 | 7.8018 | 29.5754 | 28.026 | 21.1106 | 22.221 | 21.6658 | 21.9567
| AE303 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 6.483 | 0 | 6.483 | 48.02 | 2.188 | 2.366 |  | Humidity ratio (g/gda) | 0.000262 | 0.001549 | 0.001549 | 0.001549 | 0.001549 | 0.001549 | 0.001549 | 0.002253 | 0.002454 | 0.002354 | 0.002354
| AE304 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 10.034 | 6.629 | 16.662 | 100 | 0.915 | 1.419 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE305 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.195 | 0 | 9.195 | 65.57 | 2.188 | 2.366 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE306 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.652 | 5.75 | 14.403 | 100 | 2.188 | 2.366 |  | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307 | Aug 7, 2015: Zone air mass flows set to "NA" by JN
| AE326 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.096 | 12.558 | 20.654 | 100 | 2.188 | 2.366 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8401 | 20.8401 | 12.199 | 12.7808 | 19.1006 | 18.637 | 23.3314 | 24.442 | 23.8867 | 24.1776 | Matches most recent output template.
| AE345 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.529 | 0 | 9.529 | 51.1 | 2.188 | 2.366 |  | Humidity ratio (g/gda) | 0.002947 | 0.004234 | 0.004234 | 0.004234 | 0.004234 | 0.004234 | 0.004234 | 0.004938 | 0.005139 | 0.005039 | 0.005039
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5681 | 25.5681 | 12.199 | 12.7808 | 15.4247 | 16.2939 | 23.8893 | 25.001 | 24.4447 | 24.7356
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.012443 | 0.012443 | 0.008891 | 0.008891 | 0.008891 | 0.008891 | 0.009595 | 0.009796 | 0.009695 | 0.009695
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4554 | 24.4554 | 12.199 | 12.7808 | 19.1006 | 18.6371 | 23.3314 | 24.4419 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.005795 | 0.005795 | 0.005795 | 0.005795 | 0.005795 | 0.005795 | 0.006499 | 0.0067 | 0.0066 | 0.0066
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7247 | 23.7247 | 12.199 | 12.7808 | 19.1006 | 18.6371 | 23.3314 | 24.4419 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.011971 | 0.011971 | 0.008888 | 0.008888 | 0.008888 | 0.008888 | 0.009592 | 0.009793 | 0.009693 | 0.009693
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.199 | 12.7808 | 19.1006 | 18.637 | 23.3314 | 24.442 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.015616 | 0.015616 | 0.008909 | 0.008909 | 0.008909 | 0.008909 | 0.009613 | 0.009814 | 0.009713 | 0.009713
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.199 | 12.7808 | 19.1006 | 18.6371 | 23.3314 | 24.4419 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.005212 | 0.005413 | 0.005312 | 0.005312
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 10.451 | 0 | 0 | 0 | 4.17 | 4.524 | 4.926 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.22 | 7.22 | 7.3103 | 46.5047 | 35.7662 | 21.1103 | 22.2208 | #N/A | #N/A
| AE403 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 1.399 | 0 | 1.399 | 35.98 | 0 | 0 |  | Humidity ratio (g/gda) | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.002374 | 0.002374 | #N/A | #N/A
| AE404 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 7.333 | 6.313 | 13.645 | 100 | 0 | 0 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE405 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.111 | 0 | 4.111 | 53.05 | 0 | 0 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE406 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.567 | 4.868 | 8.435 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.11327 | 0.1699 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.516 | 5.456 | 8.972 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7759 | 16.7759 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9482
| AE445 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.16 | 0 | 4.16 | 49.58 | 0 | 0 |  | Humidity ratio (g/gda) | 0.002947 | 0.003265 | 0.003265 | 0.00326 | 0.003265 | 0.003265 | 0.003265 | 0.005021 | 0.005084 | 0.005037 | 0.005055
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | #N/A | #N/A | 0.05055 | 0.05037
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.744 | 25.744 | 12.47 | 12.7846 | 12.7846 | 12.7846 | 23.8934 | 25.0043 | 24.3776 | 24.4762
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.013639 | 0.013639 | 0.009056 | 0.009056 | 0.009056 | 0.009056 | 0.00998 | 0.010327 | 0.010131 | 0.010131
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.54137 | 0.54137 | 0.54137 | 0.54137 | 0.25892 | 0.28245 | #N/A | #N/A | 0.25821 | 0.25821
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7562 | 24.7562 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9482
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004826 | 0.004826 | 0.00482 | 0.004826 | 0.004826 | 0.004826 | 0.006582 | 0.006645 | 0.006616 | 0.006616
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | #N/A | #N/A | 0.05037 | 0.05037
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1432 | 23.1432 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4432 | 23.9365 | 23.9482
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.014914 | 0.014914 | 0.009175 | 0.009175 | 0.009175 | 0.009175 | 0.010931 | 0.010994 | 0.010966 | 0.010966
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | #N/A | #N/A | 0.05037 | 0.05037
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9481
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.015616 | 0.015616 | 0.009184 | 0.009184 | 0.009184 | 0.009184 | 0.01094 | 0.011003 | 0.010974 | 0.010974
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | #N/A | #N/A | 0.05037 | 0.05037
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9482
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.006264 | 0.006327 | 0.006298 | 0.006298
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | #N/A | #N/A | 0.05037 | 0.05037
* n/a = not applicable

## TRNSYS
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | TRNSYS 17.01.0028 with TESS Libraries (and custom types) | [5 empty] | Thermal Energy System Specialists
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | TESS
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | TRNSYS
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2014-11-18 |  | Model / Organization Indentifier for Charts (short): |  |  |  | TRNSYS/TESS
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | TRNSYS with TESS Libraries
| Version: | 17.01.0028
| Date: | 2014-11-18
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.931 | 0 | 0.5861 | 8.4159 | 0 | 0 | 0 | 6.3531 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.0054 | 29.309 | 29.309 | 29.9147 | 21.1138 | 21.1138
| AE103 | 0 | 1.465 | 0.5861 | 0 | 0.78002 | 0 | 0.78002 | 32.8657 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0022906 | 0.0022906
| AE104 | 0 | 2.931 | 0.5861 | 0 | 3.4932 | 2.0544 | 5.5475 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9366 | 787.163 | 859.0292 | 859.0292 | 856.5396 | 836.6855 | 836.6855
[16 empty] | Enthalpy (J/gda) | -28.5404 | 8.0312 | 33.5617 | 33.5617 | 34.1729 | 27.0593 | 27.0593
[16 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32964 | 0.32964 | 0.32964 | 0.32964 | #N/A | 0.21683
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7694 | 20.7694 | 18.5094 | 19.0931 | 23.3325 | 23.3325
[16 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0050086 | 0.0050086
[16 empty] | Specific volume (L/kgda) | 821.5721 | 838.436 | 838.436 | 831.9891 | 829.5769 | 846.6643 | 846.6643
[16 empty] | Enthalpy (J/gda) | 23.0203 | 31.8897 | 31.8897 | 29.598 | 30.1899 | 36.2163 | 36.2163
[16 empty] | Mass flow rate (kgda/s) | 0.11148 | 0.34036 | 0.34036 | 0.34036 | 0.34035 | #N/A | 0.22887
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8689 | 24.8689 | 14.9489 | 15.5247 | 23.8905 | 23.8905
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013062 | 0.013062 | 0.010612 | 0.010612 | 0.011291 | 0.011291
[16 empty] | Specific volume (L/kgda) | 872.9312 | 861.9835 | 861.9835 | 830.0764 | 827.6673 | 856.7579 | 856.7579
[16 empty] | Enthalpy (J/gda) | 69.8514 | 58.2895 | 58.2895 | 41.874 | 42.4646 | 52.7745 | 52.7745
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34114 | 0.34114 | 0.34114 | 0.34114 | #N/A | 0.23097
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.931 | 0 | 0.5861 | 8.3563 | 0 | 0 | 0 | 6.3531 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.1845 | 29.309 | 29.309 | 29.9147 | 21.1138 | 21.1138 | 21.3858
| AE203 | 0 | 1.465 | 0.5861 | 0 | 0.85249 | 0 | 0.85249 | 32.8591 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0022906 | 0.0022906 | 0.0022906
| AE204 | 0 | 2.931 | 0.5861 | 0 | 3.5705 | 2.0544 | 5.6249 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9366 | 787.6718 | 859.0292 | 859.0292 | 856.5396 | 836.6855 | 836.6855 | 835.563
| AE205 | 0 | 1.465 | 0.5861 | 0 | 1.9128 | 0 | 1.9128 | 44.5861 | [6 empty] | Enthalpy (J/gda) | -28.5404 | 8.2119 | 33.5617 | 33.5617 | 34.1729 | 27.0593 | 27.0593 | 27.3341
| AE206 | 0 | 1.465 | 0.5861 | 0 | 1.7033 | 0.96766 | 2.6709 | 100 | [6 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32964 | 0.32964 | 0.32964 | 0.32964 | #N/A | 0.21683 | 0.21683
| AE226 | 0 | 1.465 | 0.5861 | 0 | 1.5603 | 1.7951 | 3.3553 | 100 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9827 | 20.9827 | 18.5127 | 19.0964 | 23.3358 | 23.3358 | 23.6483
| AE245 | 0 | 1.465 | 0.5861 | 0 | 2.209 | 0 | 2.209 | 34.1009 | [6 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0050086 | 0.0050086 | 0.0050086
[16 empty] | Specific volume (L/kgda) | 821.5721 | 839.0444 | 839.0444 | 831.9985 | 829.5862 | 846.6738 | 846.6738 | 845.3778
[16 empty] | Enthalpy (J/gda) | 23.0203 | 32.106 | 32.106 | 29.6013 | 30.1932 | 36.2197 | 36.2197 | 36.537
[16 empty] | Mass flow rate (kgda/s) | 0.11148 | 0.34036 | 0.34036 | 0.34036 | 0.34035 | #N/A | 0.22887 | 0.22887
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.089 | 25.089 | 14.949 | 15.5247 | 23.8905 | 23.8905 | 24.2165
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013062 | 0.013062 | 0.010612 | 0.010612 | 0.011291 | 0.011291 | 0.011291
[16 empty] | Specific volume (L/kgda) | 872.9312 | 862.62 | 862.62 | 830.0765 | 827.6674 | 856.758 | 856.758 | 855.3891
[16 empty] | Enthalpy (J/gda) | 69.8514 | 58.5163 | 58.5163 | 41.8741 | 42.4647 | 52.7746 | 52.7746 | 53.1094
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34114 | 0.34114 | 0.34114 | 0.34114 | #N/A | 0.23097 | 0.23097
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0489 | 24.0489 | 18.5089 | 19.0924 | 23.3302 | 23.3302 | 23.6425
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0058881 | 0.0058881 | 0.0058881 | 0.0058881 | 0.0065687 | 0.0065687 | 0.0065687
[16 empty] | Specific volume (L/kgda) | 850.4379 | 849.9007 | 849.9007 | 834.0579 | 831.6391 | 848.7645 | 848.7645 | 847.465
[16 empty] | Enthalpy (J/gda) | 36.4891 | 39.1826 | 39.1826 | 33.5487 | 34.1421 | 40.1835 | 40.1835 | 40.5015
[16 empty] | Mass flow rate (kgda/s) | 0.11121 | 0.33952 | 0.33952 | 0.33952 | 0.33951 | #N/A | 0.2283 | 0.2283
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4334 | 23.4334 | 18.5234 | 19.1059 | 23.3365 | 23.3365 | 23.6483
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014551 | 0.014551 | 0.013376 | 0.013376 | 0.014065 | 0.014065 | 0.014065
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.8435 | 859.8435 | 844.0471 | 841.5963 | 858.9055 | 858.9055 | 857.5889
[16 empty] | Enthalpy (J/gda) | 62.7079 | 60.6005 | 60.6005 | 52.5481 | 53.1486 | 59.2623 | 59.2623 | 59.5841
[16 empty] | Mass flow rate (kgda/s) | 0.1099 | 0.3355 | 0.3355 | 0.3355 | 0.33549 | #N/A | 0.2256 | 0.2256
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.52 | 19.1025 | 23.3331 | 23.3331 | 23.6449
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.013373 | 0.013373 | 0.014062 | 0.014062 | 0.014062
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.942 | 859.942 | 844.0335 | 841.5827 | 858.8916 | 858.8916 | 857.5751
[16 empty] | Enthalpy (J/gda) | 62.7079 | 62.7079 | 62.7079 | 52.5373 | 53.1378 | 59.2514 | 59.2514 | 59.5732
[16 empty] | Mass flow rate (kgda/s) | 0.3355 | 0.3355 | 0.3355 | 0.3355 | 0.3355 | #N/A | 0.2256 | 0.2256
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5 | 19.0837 | 23.3227 | 23.3227 | 23.6352
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.00517 | 0.00517 | 0.00517
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4379 | 850.4379 | 832.1765 | 829.7636 | 846.8544 | 846.8544 | 845.558
[16 empty] | Enthalpy (J/gda) | 36.4891 | 36.4891 | 36.4891 | 29.9972 | 30.5893 | 36.617 | 36.617 | 36.9343
[16 empty] | Mass flow rate (kgda/s) | 0.34028 | 0.34028 | 0.34028 | 0.34028 | 0.34028 | #N/A | 0.22882 | 0.22882
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 2.9467 | 0 | 0 | 0 | 24.6351 | 7.7093 | 8.3843 | AE301 | Dry bulb temperature (°C) | -29 | 3.4295 | 7.22 | 7.22 | 7.7815 | 29.27 | 27.81 | 21.1102 | 22.2171 | 21.6678 | 22.0159
| AE303 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 6.7255 | 0 | 6.7255 | 48.1783 | 2.2552 | 2.4545 |  | Humidity ratio (g/gda) | 0.00025893 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0021868 | 0.0023719 | 0.00228 | 0.00228
| AE304 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 10.315 | 6.2615 | 16.5765 | 100 | 0.99153 | 1.5236 |  | Specific volume (L/kgda) | 691.9366 | 785.4602 | 796.2249 | 796.2249 | 793.9174 | 858.8449 | 854.6986 | 836.5361 | 839.9318 | 838.2465 | 836.8112
| AE305 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.3734 | 0 | 9.3734 | 65.7465 | 2.2567 | 2.4562 |  | Enthalpy (J/gda) | -28.5404 | 7.3163 | 11.1404 | 11.1404 | 11.7069 | 33.386 | 31.913 | 26.7919 | 28.3805 | 27.592 | 27.9436
| AE306 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.9149 | 5.4435 | 14.3584 | 100 | 2.2618 | 2.4621 |  | Mass flow rate (kgda/s) | 0.2814 | 0.77055 | 0.77055 | 0.77055 | 0.77055 | 0.35561 | 0.41494 | #N/A | #N/A | 0.48915 | 0.48915
| AE326 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.4705 | 12.3053 | 20.7757 | 100 | 2.2668 | 2.4678 | AE303 | Dry bulb temperature (°C) | 15.5 | 21.015 | 21.015 | 12.215 | 12.7861 | 19.18 | 18.75 | 23.3285 | 24.4389 | 23.8872 | 24.2266
| AE345 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.7073 | 0 | 9.7073 | 51.1113 | 2.2607 | 2.461 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0048998 | 0.0050898 | 0.0049954 | 0.0049954
[16 empty] | Specific volume (L/kgda) | 821.5721 | 839.0106 | 839.0106 | 813.9115 | 811.5517 | 833.7769 | 832.5505 | 846.506 | 849.9339 | 848.2307 | 846.8233
[16 empty] | Enthalpy (J/gda) | 23.0203 | 31.9 | 31.9 | 22.9778 | 23.5569 | 30.0395 | 29.6035 | 35.9355 | 37.5464 | 36.746 | 37.0906
[16 empty] | Mass flow rate (kgda/s) | 0.27808 | 0.7538 | 0.7538 | 0.7538 | 0.7538 | 0.34788 | 0.40592 | #N/A | #N/A | 0.47572 | 0.47572
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5714 | 25.5714 | 12.2114 | 12.7819 | 15.59 | 16.48 | 23.8806 | 25.0027 | 24.4454 | 24.7871
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.012255 | 0.012255 | 0.0088543 | 0.0088543 | 0.0088543 | 0.0088543 | 0.0095252 | 0.0097162 | 0.0096213 | 0.0096213
[16 empty] | Specific volume (L/kgda) | 872.9312 | 862.9176 | 862.9176 | 819.9046 | 817.5256 | 829.612 | 832.1692 | 854.3402 | 857.8271 | 856.095 | 854.6649
[16 empty] | Enthalpy (J/gda) | 69.8514 | 56.9571 | 56.9571 | 34.6305 | 35.2138 | 38.085 | 38.995 | 48.2695 | 49.9048 | 49.0924 | 49.4423
[16 empty] | Mass flow rate (kgda/s) | 0.27553 | 0.74829 | 0.74829 | 0.74829 | 0.74829 | 0.34534 | 0.40296 | #N/A | #N/A | 0.47277 | 0.47277
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4732 | 24.4732 | 12.2132 | 12.7841 | 19.18 | 18.75 | 23.3269 | 24.4367 | 23.8854 | 24.2247
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0064597 | 0.0066501 | 0.0065555 | 0.0065555
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.9864 | 850.9864 | 815.9317 | 813.5654 | 835.8517 | 834.6222 | 848.608 | 852.0428 | 850.3362 | 848.9249
[16 empty] | Enthalpy (J/gda) | 36.4891 | 39.3742 | 39.3742 | 26.9085 | 27.489 | 33.9922 | 33.555 | 39.9028 | 41.5175 | 40.7152 | 41.0606
[16 empty] | Mass flow rate (kgda/s) | 0.27739 | 0.75194 | 0.75194 | 0.75194 | 0.75194 | 0.34702 | 0.40492 | #N/A | #N/A | 0.47454 | 0.47454
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7738 | 23.7738 | 12.2138 | 12.7843 | 19.19 | 18.76 | 23.3339 | 24.4427 | 23.8919 | 24.2309
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.01181 | 0.01181 | 0.0088557 | 0.0088557 | 0.0088557 | 0.0088557 | 0.0095248 | 0.0097161 | 0.0096211 | 0.0096211
[16 empty] | Specific volume (L/kgda) | 859.942 | 857.1235 | 857.1235 | 819.9131 | 817.5341 | 839.9574 | 838.7219 | 852.7674 | 856.2158 | 854.5024 | 853.0834
[16 empty] | Enthalpy (J/gda) | 62.7079 | 53.9762 | 53.9762 | 34.6363 | 35.2197 | 41.7693 | 41.3297 | 47.7088 | 49.3311 | 48.525 | 48.8722
[16 empty] | Mass flow rate (kgda/s) | 0.27604 | 0.74829 | 0.74829 | 0.74829 | 0.74829 | 0.34533 | 0.40295 | #N/A | #N/A | 0.47224 | 0.47224
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2 | 12.7705 | 19.19 | 18.76 | 23.3337 | 24.4424 | 23.8916 | 24.2307
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.0088476 | 0.0088476 | 0.0088476 | 0.0088476 | 0.0095166 | 0.009708 | 0.0096129 | 0.0096129
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.942 | 859.942 | 819.863 | 817.4842 | 839.9466 | 838.7111 | 852.7558 | 856.2039 | 854.4907 | 853.0715
[16 empty] | Enthalpy (J/gda) | 62.7079 | 62.7079 | 62.7079 | 34.6018 | 35.185 | 41.7487 | 41.3091 | 47.6878 | 49.31 | 48.504 | 48.8512
[16 empty] | Mass flow rate (kgda/s) | 0.74833 | 0.74833 | 0.74833 | 0.74833 | 0.74833 | 0.34536 | 0.40298 | #N/A | #N/A | 0.47229 | 0.47229
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.2 | 12.7711 | 19.18 | 18.75 | 23.328 | 24.4382 | 23.8867 | 24.2261
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0051553 | 0.0053453 | 0.0052509 | 0.0052509
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4379 | 850.4379 | 814.2005 | 811.8397 | 834.1168 | 832.8898 | 846.8497 | 850.2785 | 848.5748 | 847.1665
[16 empty] | Enthalpy (J/gda) | 36.4891 | 36.4891 | 36.4891 | 23.6068 | 24.186 | 30.687 | 30.2508 | 36.5851 | 38.1965 | 37.3958 | 37.7406
[16 empty] | Mass flow rate (kgda/s) | 0.75354 | 0.75354 | 0.75354 | 0.75354 | 0.75354 | 0.34776 | 0.40578 | #N/A | #N/A | 0.47557 | 0.47557
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 10.2578 | 0 | 0 | 0 | 4.1464 | 4.4895 | 4.8689 | AE401 | Dry bulb temperature (°C) | -29 | -28.9976 | 7.22 | 7.22 | 7.2949 | 46.8281 | 35.9884 | 21.1151 | 22.2211 | #N/A | #N/A | Aug 7, 2015: Entries replaced with "NA" by JN
| AE403 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 1.4476 | 0 | 1.4476 | 36.3722 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025893 | 0.00025899 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00026343 | 0.00025893 | 0.0022691 | 0.0022892 | #N/A | #N/A | Air property output not appropriate for 0 RA mass flow.
| AE404 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 7.3862 | 5.9214 | 13.3076 | 100 | 0 | 0 |  | Specific volume (L/kgda) | 691.9366 | 691.9435 | 794.5864 | 794.5864 | 794.2783 | 906.845 | 876.1179 | 836.6603 | 839.8318 | #N/A | #N/A
| AE405 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.091 | 0 | 4.091 | 53.4325 | 0 | 0 |  | Enthalpy (J/gda) | -28.5404 | -28.5378 | 7.9144 | 7.9144 | 7.9897 | 47.7909 | 36.8692 | 27.006 | 28.1742 | #N/A | #N/A
| AE406 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.6296 | 4.5892 | 8.2187 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.2814 | 0.2814 | 0.2814 | 0.2814 | 0.2814 | 0.11282 | 0.16858 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.5849 | 5.2196 | 8.8045 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9405 | 16.9405 | 12.6692 | 12.7822 | 12.7822 | 12.7822 | 23.3302 | 24.4386 | 23.9452 | 23.95
| AE445 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.1448 | 0 | 4.1448 | 49.5567 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0032912 | 0.0032912 | 0.0032904 | 0.0032889 | 0.0032889 | 0.0032889 | 0.0049882 | 0.0050489 | 0.0050219 | 0.0050219
[16 empty] | Specific volume (L/kgda) | 821.5721 | 826.1416 | 826.1416 | 813.9765 | 813.5066 | 814.2962 | 814.2962 | 846.6302 | 849.8778 | 848.4319 | 848.4118
[16 empty] | Enthalpy (J/gda) | 23.0203 | 25.3772 | 25.3772 | 21.0521 | 21.1625 | 21.1625 | 21.1625 | 36.1621 | 37.442 | 36.8722 | 36.8771
[16 empty] | Mass flow rate (kgda/s) | 0.27808 | 0.33495 | 0.33495 | 0.33495 | 0.33495 | 0.13681 | 0.19814 | #N/A | #N/A | 0.056872 | 0.056872
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.721 | 25.721 | 12.491 | 12.7811 | 12.7878 | 12.7878 | 23.8829 | 24.9989 | 24.3678 | 24.474
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013494 | 0.013494 | 0.009021 | 0.009017 | 0.009021 | 0.009021 | 0.0099213 | 0.010261 | 0.010067 | 0.010067
[16 empty] | Specific volume (L/kgda) | 872.9312 | 865.0361 | 865.0361 | 820.9246 | 819.6593 | 821.7776 | 821.7776 | 854.883 | 858.5556 | 856.4754 | 856.0296
[16 empty] | Enthalpy (J/gda) | 69.8514 | 60.2687 | 60.2687 | 35.3369 | 35.6235 | 35.6405 | 35.6405 | 49.2802 | 51.2876 | 50.1471 | 50.256
[16 empty] | Mass flow rate (kgda/s) | 0.27532 | 0.53883 | 0.53883 | 0.53883 | 0.53882 | 0.25786 | 0.28097 | #N/A | #N/A | 0.2635 | 0.2635
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7397 | 24.7397 | 12.6697 | 12.7825 | 12.7825 | 12.7825 | 23.3319 | 24.4401 | 23.9467 | 23.9515
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.004835 | 0.004835 | 0.004835 | 0.004835 | 0.004835 | 0.004835 | 0.0065372 | 0.006598 | 0.0065709 | 0.0065709
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4473 | 850.4473 | 815.9886 | 815.5201 | 816.3107 | 816.3107 | 848.7271 | 851.9817 | 850.5325 | 850.5124
[16 empty] | Enthalpy (J/gda) | 36.4891 | 37.2029 | 37.2029 | 24.9519 | 25.0664 | 25.0664 | 25.0664 | 40.1052 | 41.3882 | 40.8169 | 40.8218
[16 empty] | Mass flow rate (kgda/s) | 0.27739 | 0.33393 | 0.33393 | 0.33393 | 0.33393 | 0.13639 | 0.19754 | #N/A | #N/A | 0.056539 | 0.056539
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1572 | 23.1606 | 12.6584 | 12.7709 | 12.7709 | 12.7709 | 23.318 | 24.431 | 23.9345 | 23.9393
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014766 | 0.014801 | 0.0091221 | 0.0091221 | 0.0091221 | 0.0091221 | 0.010838 | 0.0109 | 0.010873 | 0.010873
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.3332 | 859.3905 | 821.5375 | 821.0663 | 821.8609 | 821.8609 | 854.4955 | 857.7874 | 856.3189 | 856.2989
[16 empty] | Enthalpy (J/gda) | 62.7079 | 60.8624 | 60.9557 | 35.7636 | 35.8787 | 35.8787 | 35.8787 | 51.0348 | 52.3348 | 51.7549 | 51.7598
[16 empty] | Mass flow rate (kgda/s) | 0.27552 | 0.33137 | 0.33137 | 0.33137 | 0.33137 | 0.13538 | 0.19599 | #N/A | #N/A | 0.055858 | 0.055858
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.67 | 12.7822 | 12.7822 | 12.7822 | 23.3286 | 24.4416 | 23.9452 | 23.9499
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.0091292 | 0.0091292 | 0.0091292 | 0.0091292 | 0.010844 | 0.010906 | 0.010879 | 0.010879
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.942 | 859.942 | 821.58 | 821.1102 | 821.9025 | 821.9025 | 854.534 | 857.8259 | 856.3576 | 856.3375
[16 empty] | Enthalpy (J/gda) | 62.7079 | 62.7079 | 62.7079 | 35.7933 | 35.908 | 35.908 | 35.908 | 51.0608 | 52.3607 | 51.7809 | 51.7858
[16 empty] | Mass flow rate (kgda/s) | 0.33133 | 0.33133 | 0.33133 | 0.33133 | 0.33133 | 0.13536 | 0.19597 | #N/A | #N/A | 0.055831 | 0.055831
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.67 | 12.7825 | 12.7825 | 12.7825 | 23.3321 | 24.442 | 23.9476 | 23.9524
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0061921 | 0.006253 | 0.0062259 | 0.0062259
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4379 | 850.4379 | 815.5415 | 815.0746 | 815.8626 | 815.8626 | 848.2614 | 851.5195 | 850.0683 | 850.0482
[16 empty] | Enthalpy (J/gda) | 36.4891 | 36.4891 | 36.4891 | 24.0835 | 24.1977 | 24.1977 | 24.1977 | 39.2271 | 40.5117 | 39.9395 | 39.9444
[16 empty] | Mass flow rate (kgda/s) | 0.33411 | 0.33411 | 0.33411 | 0.33411 | 0.33411 | 0.13647 | 0.19764 | #N/A | #N/A | 0.056569 | 0.056569
* n/a = not applicable

## Blank
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Blank
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | Blank
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | Blank
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: | [5 empty] | Model / Organization Indentifier for Charts (short): |  |  |  | Blank/Blank
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
Software:
Version:
Date:
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1)
| AE101 | 2.93 | [12 empty] | AE101 | Dry bulb temperature (°C)
| AE103 | [14 empty] | Humidity ratio (g/gda)
| AE104 | [14 empty] | Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE103 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE104 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.93 | [12 empty] | AE201 | Dry bulb temperature (°C)
| AE203 | [14 empty] | Humidity ratio (g/gda)
| AE204 | [14 empty] | Specific volume (L/kgda)
| AE205 | [14 empty] | Enthalpy (J/gda)
| AE206 | [14 empty] | Mass flow rate (kgda/s)
| AE226 | [13 empty] | AE203 | Dry bulb temperature (°C)
| AE245 | [14 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE204 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE205 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE206 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE226 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[15 empty] | AE245 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9307 |  |  | 2.3446 | [9 empty] | AE301 | Dry bulb temperature (°C)
| AE303 | [14 empty] | Humidity ratio (g/gda)
| AE304 | [14 empty] | Specific volume (L/kgda)
| AE305 | [14 empty] | Enthalpy (J/gda)
| AE306 | [14 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
| AE326 | [13 empty] | AE303 | Dry bulb temperature (°C)
| AE345 | [14 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE304 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE305 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE306 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE326 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE345 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
* =na()
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9307 |  |  | 2.3446 | [9 empty] | AE401 | Dry bulb temperature (°C)
| AE403 | [14 empty] | Humidity ratio (g/gda)
| AE404 | [14 empty] | Specific volume (L/kgda)
| AE405 | [14 empty] | Enthalpy (J/gda)
| AE406 | [14 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
| AE426 | [13 empty] | AE403 | Dry bulb temperature (°C)
| AE445 | [14 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE404 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE405 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE406 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE426 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
[15 empty] | AE445 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[16 empty] | Mass flow rate (kgda/s) | [7 empty] | #N/A | #N/A
* =na()