## Read Me
ASHRAE Standard 140-2023
Informative Annex B16, Section B16.7.1 Example Results
for
Section 11, Airside HVAC Tests: Fan Coil and Single Zone Systems
AE101 through AE245
This spreadsheet contains the Informative Annex B16, Section B16.7.1 example results.
Users interested in looking at the example result tables and figures should go to the "Table List"
and "Figure List" sheets for a listing of tables and figures and their locations.
This spreadsheet can also be used to compare new results with the example results.
To add new results go to sheet "Adding Results" (2nd tab), cell A6 for instructions.
Results are added to sheet "Your Data" (3rd tab) and will automatically appear in the tables and figures.
To print example results or example results with new user generated results go to sheet "Title Page"
(4th tab) and follow the instructions starting in cell B5.
SHEET GUIDE
"Read Me" : General directions to using this workbook.
"Adding Results" : Instructions for adding new results, and map to example result and "YourData" worksheets.
"YourData" : For tested program results if doing comparison
"Title Page" : Sets headers for tables and charts and provides cover sheet to example results or new comparison results; see instructions on page.
"Program List" : Documentation of simulation programs used to produce Informative Annex B16, Section B16.7.1 example results
"Table List": List of Informative Annex B16, Section B16.7.1 Tables in workbook with locations.
"Figure List": List of Informative Annex B16, Section B16.7.1 Figures in workbook with locations.
"Tables 1" through "Delta Tables 1" : Formatted result tables
"Fig B16.7.1-1 HeatCoil" through "Fig B16.7.1-22 Delta Econo" : Figures
"Detailed Location Results": Tool to compare detailed results
"Aggregate Results Final" : Unformatted results for use in tables and charts.
"Delta Results Final": Unformatted delta results for use in tables and charts.
Individual Example Results Worksheets as follows:
QAS: QAS model results set, 12Nov2014. Submitted by National Renewable Energy Laboratory, Golden, Colorado, United States.
DEEAP: DEEAP model results set, 10Dec2012. Submitted by AAON, Inc., Tulsa, Oklahoma, United States.
DeST: DeST 2 model results set, 21Nov2013. Submitted by Tsinghua University, Beijing, China.
DOE22: DOE-2.2 model results set, 10Mar2015. Submitted by National Renewable Energy Laboratory, Golden, Colorado, United States.
EPlus: EnergyPlus 8.2 model results set, 15Jan2015. Submitted by GARD Analytics, Arlington Heights, Illinois, United States.
IES-VE: IES-VE model results set, 20Feb2015. Submitted by Integrated Environmental Solutions, Glasgow, United Kingdom.
LCEM: LCEM model results set, 14Jan2015. Submitted by Ministry of Land, Infrastructure, Transportation and Tourism, Tokyo, Japan.
TRNSYS: TRNSYS-17 with TESS libraries model results set, 18Nov2014. Submitted by TESS, Madison, Wisconsin, United States.

## Adding Results
Output spreadsheet for Airside HVAC Equipment Diagnostic Tests: AE101 through AE445
New result data can be imported into this workbook and will automatically be included in tables and charts.
INSTRUCTIONS FOR ADDING NEW RESULTS
Import data so that Cell C50 of Std140_AE_Output.xlsx is in C50 of Sheet "YourData"
Check that the summary results for Case AE101 start at YourData!C61.
Data should flow to "YourData" cells as tabulated below. Your data will then appear in the rightmost column
of each table on sheets "Tables 1" to "Delta Tables 1". Charts are also updated with "your data" automatically.
Complete the program information block on "YourData", which is used for legend titles for the tables and graphs.
CELL ADDRESS GUIDE FOR EXAMPLE RESULT SHEETS AND NEW RESULTS
Gives locations for data in "YourData" sheet and in participant sheets.
Program Information Block - complete blue boxes to identify program and organization for report
| Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
| I5 | [5 empty] | O5
| Program Version Release Date: |  |  |  | I6 |  | Modeler Organization for Tables and Charts (short): |  |  |  | O6
| Program Name for Tables and Charts (short): |  |  |  | I7
| Results Submission Date: |  |  |  | I8 |  | Model / Organization Indentifier for Charts (short): |  |  |  | O8 | defaults to short program name / short organization name
Results
| Software: | C50
| Version: | C51
| Date: | C52
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | C61 | D61 | E61 | F61 | G61 | H61 | I61 | J61 | [5 empty] | AE101 | Dry bulb temperature (°C) | S61 | T61 | U61 | V61 | W61 | X61 | Y61
| AE103 | C62 | D62 | E62 | F62 | G62 | H62 | I62 | J62 | [6 empty] | Humidity ratio (g/gda) | S62 | T62 | U62 | V62 | W62 | X62 | Y62
| AE104 | C63 | D63 | E63 | F63 | G63 | H63 | I63 | J63 | [6 empty] | Specific volume (L/kgda) | S63 | T63 | U63 | V63 | W63 | X63 | Y63
[16 empty] | Enthalpy (J/gda) | S64 | T64 | U64 | V64 | W64 | X64 | Y64
[16 empty] | Mass flow rate (kgda/s) | S65 | T65 | U65 | V65 | W65 | #N/A | Y65
[15 empty] | AE103 | Dry bulb temperature (°C) | S66 | T66 | U66 | V66 | W66 | X66 | Y66
[16 empty] | Humidity ratio (g/gda) | S67 | T67 | U67 | V67 | W67 | X67 | Y67
[16 empty] | Specific volume (L/kgda) | S68 | T68 | U68 | V68 | W68 | X68 | Y68
[16 empty] | Enthalpy (J/gda) | S69 | T69 | U69 | V69 | W69 | X69 | Y69
[16 empty] | Mass flow rate (kgda/s) | S70 | T70 | U70 | V70 | W70 | #N/A | Y70
[15 empty] | AE104 | Dry bulb temperature (°C) | S71 | T71 | U71 | V71 | W71 | X71 | Y71
[16 empty] | Humidity ratio (g/gda) | S72 | T72 | U72 | V72 | W72 | X72 | Y72
[16 empty] | Specific volume (L/kgda) | S73 | T73 | U73 | V73 | W73 | X73 | Y73
[16 empty] | Enthalpy (J/gda) | S74 | T74 | U74 | V74 | W74 | X74 | Y74
[16 empty] | Mass flow rate (kgda/s) | S75 | T75 | U75 | V75 | W75 | #N/A | Y75
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | C89 | D89 | E89 | F89 | G89 | H89 | I89 | J89 | [5 empty] | AE201 | Dry bulb temperature (°C) | S89 | T89 | U89 | V89 | W89 | X89 | Y89 | Z89
| AE203 | C90 | D90 | E90 | F90 | G90 | H90 | I90 | J90 | [6 empty] | Humidity ratio (g/gda) | S90 | T90 | U90 | V90 | W90 | X90 | Y90 | Z90
| AE204 | C91 | D91 | E91 | F91 | G91 | H91 | I91 | J91 | [6 empty] | Specific volume (L/kgda) | S91 | T91 | U91 | V91 | W91 | X91 | Y91 | Z91
| AE205 | C92 | D92 | E92 | F92 | G92 | H92 | I92 | J92 | [6 empty] | Enthalpy (J/gda) | S92 | T92 | U92 | V92 | W92 | X92 | Y92 | Z92
| AE206 | C93 | D93 | E93 | F93 | G93 | H93 | I93 | J93 | [6 empty] | Mass flow rate (kgda/s) | S93 | T93 | U93 | V93 | W93 | #N/A | Y93 | Z93
| AE226 | C94 | D94 | E94 | F94 | G94 | H94 | I94 | J94 | [5 empty] | AE203 | Dry bulb temperature (°C) | S94 | T94 | U94 | V94 | W94 | X94 | Y94 | Z94
| AE245 | C95 | D95 | E95 | F95 | G95 | H95 | I95 | J95 | [6 empty] | Humidity ratio (g/gda) | S95 | T95 | U95 | V95 | W95 | X95 | Y95 | Z95
[16 empty] | Specific volume (L/kgda) | S96 | T96 | U96 | V96 | W96 | X96 | Y96 | Z96
[16 empty] | Enthalpy (J/gda) | S97 | T97 | U97 | V97 | W97 | X97 | Y97 | Z97
[16 empty] | Mass flow rate (kgda/s) | S98 | T98 | U98 | V98 | W98 | #N/A | Y98 | Z98
[15 empty] | AE204 | Dry bulb temperature (°C) | S99 | T99 | U99 | V99 | W99 | X99 | Y99 | Z99
[16 empty] | Humidity ratio (g/gda) | S100 | T100 | U100 | V100 | W100 | X100 | Y100 | Z100
[16 empty] | Specific volume (L/kgda) | S101 | T101 | U101 | V101 | W101 | X101 | Y101 | Z101
[16 empty] | Enthalpy (J/gda) | S102 | T102 | U102 | V102 | W102 | X102 | Y102 | Z102
[16 empty] | Mass flow rate (kgda/s) | S103 | T103 | U103 | V103 | W103 | #N/A | Y103 | Z103
[15 empty] | AE205 | Dry bulb temperature (°C) | S104 | T104 | U104 | V104 | W104 | X104 | Y104 | Z104
[16 empty] | Humidity ratio (g/gda) | S105 | T105 | U105 | V105 | W105 | X105 | Y105 | Z105
[16 empty] | Specific volume (L/kgda) | S106 | T106 | U106 | V106 | W106 | X106 | Y106 | Z106
[16 empty] | Enthalpy (J/gda) | S107 | T107 | U107 | V107 | W107 | X107 | Y107 | Z107
[16 empty] | Mass flow rate (kgda/s) | S108 | T108 | U108 | V108 | W108 | #N/A | Y108 | Z108
[15 empty] | AE206 | Dry bulb temperature (°C) | S109 | T109 | U109 | V109 | W109 | X109 | Y109 | Z109
[16 empty] | Humidity ratio (g/gda) | S110 | T110 | U110 | V110 | W110 | X110 | Y110 | Z110
[16 empty] | Specific volume (L/kgda) | S111 | T111 | U111 | V111 | W111 | X111 | Y111 | Z111
[16 empty] | Enthalpy (J/gda) | S112 | T112 | U112 | V112 | W112 | X112 | Y112 | Z112
[16 empty] | Mass flow rate (kgda/s) | S113 | T113 | U113 | V113 | W113 | #N/A | Y113 | Z113
[15 empty] | AE226 | Dry bulb temperature (°C) | S114 | T114 | U114 | V114 | W114 | X114 | Y114 | Z114
[16 empty] | Humidity ratio (g/gda) | S115 | T115 | U115 | V115 | W115 | X115 | Y115 | Z115
[16 empty] | Specific volume (L/kgda) | S116 | T116 | U116 | V116 | W116 | X116 | Y116 | Z116
[16 empty] | Enthalpy (J/gda) | S117 | T117 | U117 | V117 | W117 | X117 | Y117 | Z117
[16 empty] | Mass flow rate (kgda/s) | S118 | T118 | U118 | V118 | W118 | #N/A | Y118 | Z118
[15 empty] | AE245 | Dry bulb temperature (°C) | S119 | T119 | U119 | V119 | W119 | X119 | Y119 | Z119
[16 empty] | Humidity ratio (g/gda) | S120 | T120 | U120 | V120 | W120 | X120 | Y120 | Z120
[16 empty] | Specific volume (L/kgda) | S121 | T121 | U121 | V121 | W121 | X121 | Y121 | Z121
[16 empty] | Enthalpy (J/gda) | S122 | T122 | U122 | V122 | W122 | X122 | Y122 | Z122
[16 empty] | Mass flow rate (kgda/s) | S123 | T123 | U123 | V123 | W123 | #N/A | Y123 | Z123
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | C137 | D137 | E137 | F137 | G137 | H137 | I137 | J137 | K137 | L137 | M137 | N137 | O137 | AE301 | Dry bulb temperature (°C) | S137 | T137 | U137 | V137 | W137 | X137 | Y137 | Z137 | AA137 | AB137 | AC137
| AE303 | C138 | D138 | E138 | F138 | G138 | H138 | I138 | J138 | K138 | L138 | M138 | N138 | O138 |  | Humidity ratio (g/gda) | S138 | T138 | U138 | V138 | W138 | X138 | Y138 | Z138 | AA138 | AB138 | AC138
| AE304 | C139 | D139 | E139 | F139 | G139 | H139 | I139 | J139 | K139 | L139 | M139 | N139 | O139 |  | Specific volume (L/kgda) | S139 | T139 | U139 | V139 | W139 | X139 | Y139 | Z139 | AA139 | AB139 | AC139
| AE305 | C140 | D140 | E140 | F140 | G140 | H140 | I140 | J140 | K140 | L140 | M140 | N140 | O140 |  | Enthalpy (J/gda) | S140 | T140 | U140 | V140 | W140 | X140 | Y140 | Z140 | AA140 | AB140 | AC140
| AE306 | C141 | D141 | E141 | F141 | G141 | H141 | I141 | J141 | K141 | L141 | M141 | N141 | O141 |  | Mass flow rate (kgda/s) | S141 | T141 | U141 | V141 | W141 | X141 | Y141 | #N/A | #N/A | AB141 | AC141
| AE326 | C142 | D142 | E142 | F142 | G142 | H142 | I142 | J142 | K142 | L142 | M142 | N142 | O142 | AE303 | Dry bulb temperature (°C) | S142 | T142 | U142 | V142 | W142 | X142 | Y142 | Z142 | AA142 | AB142 | AC142
| AE345 | C143 | D143 | E143 | F143 | G143 | H143 | I143 | J143 | K143 | L143 | M143 | N143 | O143 |  | Humidity ratio (g/gda) | S143 | T143 | U143 | V143 | W143 | X143 | Y143 | Z143 | AA143 | AB143 | AC143
[16 empty] | Specific volume (L/kgda) | S144 | T144 | U144 | V144 | W144 | X144 | Y144 | Z144 | AA144 | AB144 | AC144
[16 empty] | Enthalpy (J/gda) | S145 | T145 | U145 | V145 | W145 | X145 | Y145 | Z145 | AA145 | AB145 | AC145
[16 empty] | Mass flow rate (kgda/s) | S146 | T146 | U146 | V146 | W146 | X146 | Y146 | #N/A | #N/A | AB146 | AC146
[15 empty] | AE304 | Dry bulb temperature (°C) | S147 | T147 | U147 | V147 | W147 | X147 | Y147 | Z147 | AA147 | AB147 | AC147
[16 empty] | Humidity ratio (g/gda) | S148 | T148 | U148 | V148 | W148 | X148 | Y148 | Z148 | AA148 | AB148 | AC148
[16 empty] | Specific volume (L/kgda) | S149 | T149 | U149 | V149 | W149 | X149 | Y149 | Z149 | AA149 | AB149 | AC149
[16 empty] | Enthalpy (J/gda) | S150 | T150 | U150 | V150 | W150 | X150 | Y150 | Z150 | AA150 | AB150 | AC150
[16 empty] | Mass flow rate (kgda/s) | S151 | T151 | U151 | V151 | W151 | X151 | Y151 | #N/A | #N/A | AB151 | AC151
[15 empty] | AE305 | Dry bulb temperature (°C) | S152 | T152 | U152 | V152 | W152 | X152 | Y152 | Z152 | AA152 | AB152 | AC152
[16 empty] | Humidity ratio (g/gda) | S153 | T153 | U153 | V153 | W153 | X153 | Y153 | Z153 | AA153 | AB153 | AC153
[16 empty] | Specific volume (L/kgda) | S154 | T154 | U154 | V154 | W154 | X154 | Y154 | Z154 | AA154 | AB154 | AC154
[16 empty] | Enthalpy (J/gda) | S155 | T155 | U155 | V155 | W155 | X155 | Y155 | Z155 | AA155 | AB155 | AC155
[16 empty] | Mass flow rate (kgda/s) | S156 | T156 | U156 | V156 | W156 | X156 | Y156 | #N/A | #N/A | AB156 | AC156
[15 empty] | AE306 | Dry bulb temperature (°C) | S157 | T157 | U157 | V157 | W157 | X157 | Y157 | Z157 | AA157 | AB157 | AC157
[16 empty] | Humidity ratio (g/gda) | S158 | T158 | U158 | V158 | W158 | X158 | Y158 | Z158 | AA158 | AB158 | AC158
[16 empty] | Specific volume (L/kgda) | S159 | T159 | U159 | V159 | W159 | X159 | Y159 | Z159 | AA159 | AB159 | AC159
[16 empty] | Enthalpy (J/gda) | S160 | T160 | U160 | V160 | W160 | X160 | Y160 | Z160 | AA160 | AB160 | AC160
[16 empty] | Mass flow rate (kgda/s) | S161 | T161 | U161 | V161 | W161 | X161 | Y161 | #N/A | #N/A | AB161 | AC161
[15 empty] | AE326 | Dry bulb temperature (°C) | S162 | T162 | U162 | V162 | W162 | X162 | Y162 | Z162 | AA162 | AB162 | AC162
[16 empty] | Humidity ratio (g/gda) | S163 | T163 | U163 | V163 | W163 | X163 | Y163 | Z163 | AA163 | AB163 | AC163
[16 empty] | Specific volume (L/kgda) | S164 | T164 | U164 | V164 | W164 | X164 | Y164 | Z164 | AA164 | AB164 | AC164
[16 empty] | Enthalpy (J/gda) | S165 | T165 | U165 | V165 | W165 | X165 | Y165 | Z165 | AA165 | AB165 | AC165
[16 empty] | Mass flow rate (kgda/s) | S166 | T166 | U166 | V166 | W166 | X166 | Y166 | #N/A | #N/A | AB166 | AC166
[15 empty] | AE345 | Dry bulb temperature (°C) | S167 | T167 | U167 | V167 | W167 | X167 | Y167 | Z167 | AA167 | AB167 | AC167
[16 empty] | Humidity ratio (g/gda) | S168 | T168 | U168 | V168 | W168 | X168 | Y168 | Z168 | AA168 | AB168 | AC168
[16 empty] | Specific volume (L/kgda) | S169 | T169 | U169 | V169 | W169 | X169 | Y169 | Z169 | AA169 | AB169 | AC169
[16 empty] | Enthalpy (J/gda) | S170 | T170 | U170 | V170 | W170 | X170 | Y170 | Z170 | AA170 | AB170 | AC170
[16 empty] | Mass flow rate (kgda/s) | S171 | T171 | U171 | V171 | W171 | X171 | Y171 | #N/A | #N/A | AB171 | AC171
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | C164 | D164 | E164 | F164 | G164 | H164 | I164 | J164 | K164 | L164 | M164 | N164 | O164 | AE401 | Dry bulb temperature (°C) | S185 | T185 | U185 | V185 | W185 | X185 | Y185 | Z185 | AA185 | AB185 | AC185
| AE403 | C165 | D165 | E165 | F165 | G165 | H165 | I165 | J165 | K165 | L165 | M165 | N165 | O165 |  | Humidity ratio (g/gda) | S186 | T186 | U186 | V186 | W186 | X186 | Y186 | Z186 | AA186 | AB186 | AC186
| AE404 | C166 | D166 | E166 | F166 | G166 | H166 | I166 | J166 | K166 | L166 | M166 | N166 | O166 |  | Specific volume (L/kgda) | S187 | T187 | U187 | V187 | W187 | X187 | Y187 | Z187 | AA187 | AB187 | AC187
| AE405 | C167 | D167 | E167 | F167 | G167 | H167 | I167 | J167 | K167 | L167 | M167 | N167 | O167 |  | Enthalpy (J/gda) | S188 | T188 | U188 | V188 | W188 | X188 | Y188 | Z188 | AA188 | AB188 | AC188
| AE406 | C168 | D168 | E168 | F168 | G168 | H168 | I168 | J168 | K168 | L168 | M168 | N168 | O168 |  | Mass flow rate (kgda/s) | S189 | T189 | U189 | V189 | W189 | X189 | Y189 | #N/A | #N/A | AB189 | AC189
| AE426 | C169 | D169 | E169 | F169 | G169 | H169 | I169 | J169 | K169 | L169 | M169 | N169 | O169 | AE403 | Dry bulb temperature (°C) | S190 | T190 | U190 | V190 | W190 | X190 | Y190 | Z190 | AA190 | AB190 | AC190
| AE445 | C170 | D170 | E170 | F170 | G170 | H170 | I170 | J170 | K170 | L170 | M170 | N170 | O170 |  | Humidity ratio (g/gda) | S191 | T191 | U191 | V191 | W191 | X191 | Y191 | Z191 | AA191 | AB191 | AC191
[16 empty] | Specific volume (L/kgda) | S192 | T192 | U192 | V192 | W192 | X192 | Y192 | Z192 | AA192 | AB192 | AC192
[16 empty] | Enthalpy (J/gda) | S193 | T193 | U193 | V193 | W193 | X193 | Y193 | Z193 | AA193 | AB193 | AC193
[16 empty] | Mass flow rate (kgda/s) | S194 | T194 | U194 | V194 | W194 | X194 | Y194 | #N/A | #N/A | AB194 | AC194
[15 empty] | AE404 | Dry bulb temperature (°C) | S195 | T195 | U195 | V195 | W195 | X195 | Y195 | Z195 | AA195 | AB195 | AC195
[16 empty] | Humidity ratio (g/gda) | S196 | T196 | U196 | V196 | W196 | X196 | Y196 | Z196 | AA196 | AB196 | AC196
[16 empty] | Specific volume (L/kgda) | S197 | T197 | U197 | V197 | W197 | X197 | Y197 | Z197 | AA197 | AB197 | AC197
[16 empty] | Enthalpy (J/gda) | S198 | T198 | U198 | V198 | W198 | X198 | Y198 | Z198 | AA198 | AB198 | AC198
[16 empty] | Mass flow rate (kgda/s) | S199 | T199 | U199 | V199 | W199 | X199 | Y199 | #N/A | #N/A | AB199 | AC199
[15 empty] | AE405 | Dry bulb temperature (°C) | S200 | T200 | U200 | V200 | W200 | X200 | Y200 | Z200 | AA200 | AB200 | AC200
[16 empty] | Humidity ratio (g/gda) | S201 | T201 | U201 | V201 | W201 | X201 | Y201 | Z201 | AA201 | AB201 | AC201
[16 empty] | Specific volume (L/kgda) | S202 | T202 | U202 | V202 | W202 | X202 | Y202 | Z202 | AA202 | AB202 | AC202
[16 empty] | Enthalpy (J/gda) | S203 | T203 | U203 | V203 | W203 | X203 | Y203 | Z203 | AA203 | AB203 | AC203
[16 empty] | Mass flow rate (kgda/s) | S204 | T204 | U204 | V204 | W204 | X204 | Y204 | #N/A | #N/A | AB204 | AC204
[15 empty] | AE406 | Dry bulb temperature (°C) | S205 | T205 | U205 | V205 | W205 | X205 | Y205 | Z205 | AA205 | AB205 | AC205
[16 empty] | Humidity ratio (g/gda) | S206 | T206 | U206 | V206 | W206 | X206 | Y206 | Z206 | AA206 | AB206 | AC206
[16 empty] | Specific volume (L/kgda) | S207 | T207 | U207 | V207 | W207 | X207 | Y207 | Z207 | AA207 | AB207 | AC207
[16 empty] | Enthalpy (J/gda) | S208 | T208 | U208 | V208 | W208 | X208 | Y208 | Z208 | AA208 | AB208 | AC208
[16 empty] | Mass flow rate (kgda/s) | S209 | T209 | U209 | V209 | W209 | X209 | Y209 | #N/A | #N/A | AB209 | AC209
[15 empty] | AE426 | Dry bulb temperature (°C) | S210 | T210 | U210 | V210 | W210 | X210 | Y210 | Z210 | AA210 | AB210 | AC210
[16 empty] | Humidity ratio (g/gda) | S211 | T211 | U211 | V211 | W211 | X211 | Y211 | Z211 | AA211 | AB211 | AC211
[16 empty] | Specific volume (L/kgda) | S212 | T212 | U212 | V212 | W212 | X212 | Y212 | Z212 | AA212 | AB212 | AC212
[16 empty] | Enthalpy (J/gda) | S213 | T213 | U213 | V213 | W213 | X213 | Y213 | Z213 | AA213 | AB213 | AC213
[16 empty] | Mass flow rate (kgda/s) | S214 | T214 | U214 | V214 | W214 | X214 | Y214 | #N/A | #N/A | AB214 | AC214
[15 empty] | AE445 | Dry bulb temperature (°C) | S215 | T215 | U215 | V215 | W215 | X215 | Y215 | Z215 | AA215 | AB215 | AC215
[16 empty] | Humidity ratio (g/gda) | S216 | T216 | U216 | V216 | W216 | X216 | Y216 | Z216 | AA216 | AB216 | AC216
[16 empty] | Specific volume (L/kgda) | S217 | T217 | U217 | V217 | W217 | X217 | Y217 | Z217 | AA217 | AB217 | AC217
[16 empty] | Enthalpy (J/gda) | S218 | T218 | U218 | V218 | W218 | X218 | Y218 | Z218 | AA218 | AB218 | AC218
[16 empty] | Mass flow rate (kgda/s) | S219 | T219 | U219 | V219 | W219 | X219 | Y219 | #N/A | #N/A | AB219 | AC219

## YourData
Output spreadsheet for Airside HVAC Equipment Diagnostic Tests: AE101 through AE445
See "Adding Results" tab for more information. |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Paste new data in row 50 and below. |  |  |  | OpenSimula V 0.5 | [5 empty] | University of Seville
Cells in blue are used in titles and labels |  |  |  | Program Version Release Date: |  |  |  | 2025-05-01 |  | Modeler Organization for Tables and Charts (short): |  |  |  | US
Editing them here flows thru to other tabs |  |  |  | Program Name for Tables and Charts (short): |  |  |  | OpenSimula
To print pdf file, see instructions on "Read Me" tab. |  |  |  | Results Submission Date: |  |  |  | 2025-03-14 |  | Model / Organization Indentifier for Charts (short): |  |  |  | OpenSimula/US | defaults to short program name / short organization name
Content Instructions
1. Use specified units
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| C61...J63: | Coil Loads, Fan Coil Air System, AE100 Series Cases
| S61...Y75: | Detailed Outputs, Fan Coil Air System, AE100 Series Cases
| C89...J95: | Coil Loads, Single Zone Air System, AE200 Series Cases
| S89...Z123: | Detailed Outputs, Single Zone Air System, AE200 Series Cases
| C137...O143: | Coil Loads, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| S137...AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| C185...O191: | Coil Loads, Variable Air Volume Air System, AE400 Series Cases
| S185...AC219: | Detailed Outputs, Variable Air Volume Air System, AE400 Series Cases
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
[18 empty] | OA | MA | CO | SA | RA
[17 empty] | 0 | 26.9 | 24.8601 | 14.76 | 15.3465 | 23.889
[17 empty] | 1 | 0.016766 | 0.012863 | 0.010316 | 0.010316 | 0.011004
| Software: | OpenSimula | [14 empty] | 2 | 872.9203 | 861.689 | 829.1446 | 830.8336 | 856.3651
| Version: | 0.5 | [14 empty] | 3 | 69.831 | 57.7755 | 40.9333 | 41.5345 | 52.042
| Date: | 9-apr-2025 | [14 empty] | 4 | 0.11012 | 0.34145 | 0.34145 | 0.34145 | 0.23132
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 3.0195 | 0 | 0 | 8.5049 | 0 | 0 | 0 | 6.2974 | [6 empty] | AE101 | Dry bulb temperature (°C) | -29 | 3.774 | 29.702 | 29.702 | 30.3161 | 21.111 | 21.111
| AE103 | 0 | 1.449 | 0.58608 | 0 | 0.77201 | 0 | 0.77201 | 32.9843 | [7 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0016178 | 0.0016176 | 0.0016176 | 0.0016176 | 0.0023363 | 0.0023363
| AE104 | 0 | 2.9343 | 0.587 | 0 | 3.4693 | 2.1753 | 5.6446 | 98.4538 | [7 empty] | Specific volume (L/kgda) | 691.9366 | 786.5342 | 860.176 | 860.176 | 861.9203 | 836.7387 | 836.7387
[17 empty] | Enthalpy (J/gda) | -28.5404 | 7.854 | 34.0152 | 34.0152 | 34.6348 | 27.1725 | 27.1725
[17 empty] | Mass flow rate (kgda/s) | 0.11404 | 0.32961 | 0.32961 | 0.32961 | 0.32961 | n/a* | 0.21557
[16 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7693 | 18.5162 | 18.5162 | 19.1041 | 23.333 | 23.333
[17 empty] | Humidity ratio (g/gda) | 0.0029317 | 0.0043474 | 0.0043473 | 0.0043473 | 0.0043473 | 0.0050353 | 0.0050353
[17 empty] | Specific volume (L/kgda) | 821.5666 | 838.4594 | 832.0321 | 832.0321 | 833.7092 | 846.7019 | 846.7019
[17 empty] | Enthalpy (J/gda) | 23.0097 | 31.9347 | 29.6496 | 29.6496 | 30.2457 | 36.2847 | 36.2847
[17 empty] | Mass flow rate (kgda/s) | 0.11139 | 0.34034 | 0.34034 | 0.34034 | 0.34034 | n/a* | 0.22895
[16 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8601 | 14.76 | 14.76 | 15.3465 | 23.889 | 23.889
[17 empty] | Humidity ratio (g/gda) | 0.016766 | 0.012863 | 0.010316 | 0.010316 | 0.010316 | 0.011004 | 0.011004
[17 empty] | Specific volume (L/kgda) | 872.9203 | 861.689 | 829.1446 | 829.1446 | 830.8336 | 856.3651 | 856.3651
[17 empty] | Enthalpy (J/gda) | 69.831 | 57.7755 | 40.9333 | 40.9333 | 41.5345 | 52.042 | 52.042
[17 empty] | Mass flow rate (kgda/s) | 0.11012 | 0.34145 | 0.34145 | 0.34145 | 0.34145 | n/a* | 0.23132
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | [14 empty] | AE201 | Dry bulb temperature (°C)
| AE203 | [15 empty] | Humidity ratio (g/gda)
| AE204 | [15 empty] | Specific volume (L/kgda)
| AE205 | [15 empty] | Enthalpy (J/gda)
| AE206 | [15 empty] | Mass flow rate (kgda/s) | [5 empty] | n/a*
| AE226 | [14 empty] | AE203 | Dry bulb temperature (°C)
| AE245 | [15 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [5 empty] | n/a*
[16 empty] | AE204 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [5 empty] | n/a*
[16 empty] | AE205 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [5 empty] | n/a*
[16 empty] | AE206 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [5 empty] | n/a*
[16 empty] | AE226 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [5 empty] | n/a*
[16 empty] | AE245 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [5 empty] | n/a*
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 |  | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) |  | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | [14 empty] | AE301 | Dry bulb temperature (°C)
| AE303 | [15 empty] | Humidity ratio (g/gda)
| AE304 | [15 empty] | Specific volume (L/kgda)
| AE305 | [15 empty] | Enthalpy (J/gda)
| AE306 | [15 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
| AE326 | [14 empty] | AE303 | Dry bulb temperature (°C)
| AE345 | [15 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE304 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE305 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE306 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE326 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE345 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 |  | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) |  | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | [14 empty] | AE401 | Dry bulb temperature (°C)
| AE403 | [15 empty] | Humidity ratio (g/gda)
| AE404 | [15 empty] | Specific volume (L/kgda)
| AE405 | [15 empty] | Enthalpy (J/gda)
| AE406 | [15 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
| AE426 | [14 empty] | AE403 | Dry bulb temperature (°C)
| AE445 | [15 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE404 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE405 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE406 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE426 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE445 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
* n/a = not applicable

## Title Page
ASHRAE Standard 140-2023 | To print example results:
Informative Annex B16, Section B16.7.1 | 1. Select results type in cell B21:
"Example" for Airside HVAC BESTEST Example Results
Example Results | "Comparison" if comparing new user results with the example results
for | 2. Select the following sheets:
Section 11, Airside HVAC Equipment Performance Tests AE101 through AE245 | "Title Page" thru "Figure List"
"Tables 1" thru "Delta Tables 1"
"Fig B16.7.1-1 HeatCoil" through "Fig B16.7.1-22 Delta Econo"
3. Print, or Save to pdf.
The title page, and table and chart titles are based upon the selected results type,
and for comparison results, also include inputs from the program
information block of the "YourData" tab.
Results Type (Example or Comparison)
Example
Scratch area for Table Title
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.1
Scratch area for Table subtitle 1
Example Results for Section 11, Airside HVAC BESTEST Cases AE101 through AE245
Scratch area for Table subtitle 2
Scratch area for chart subtitles 1
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.1
Scratch area for chart subtitles 2
Example Results for Section 11, Airside HVAC BESTEST Cases AE101 through AE245

## Program List
ASHRAE Standard 140-2023
Computer Programs, Program Authors, and Producers of Example Results for
Section 11, Airside HVAC Equipment Performance Tests AE101 through AE245
The quasi-analytical solution and programs used to generate the example results are described in Table B17-13. The first
column of the table ("Model") indicates the program name and version number, or indicates a quasi-analytical solution.
The second column ("Authoring Organization") indicates the national research facility, university, or industry organization
with expertise in building science that wrote the simulation software.
The third column ("Implemented By") indicates the national research facility, university, or industry organization with
expertise in building science that performed the simulations or did the quasi-analytical solutions. The organizations that
performed simulations either ran software written by their organization or otherwise maintained contact with the program
authors during the project.
The fourth column ("Abbreviation") indicates the identifying abbreviation used in the results tables and figures.
See Standard 140, Informative Annex B17 for further details.
Table B17-13 Airside HVAC Cases
Participating Organizations and Models
Model | Authoring Organization | Implemented by | Abbreviation
Quasi-Analytical Solution (QAS) | PSUa/UNOb/TAMUc/NRELd/JNAe/MDKf, United States | NRELd/JNAe/MDKf, United States | QAS/PSU-TAMU-NREL
DEEAPg 1.1.2 | AAON, Inc., United States | AAON, Inc., United States | DEEAP/AAON
DeSTh 2 | Tsinghua University, China | Tsinghua University, China / LBNLi, United States | DeST/TsinghuaU-LBNL
DOE-2.2 V48L | JJHj/LBNLi/UCk, United States | NRELd/JNAe/MDKf, United States | DOE-2.2/NREL
EnergyPlus 8.2.0 | DOE-BTl, United States | GARD Analytics, Inc., United States | EnergyPlus/GARD
IES-VEm 2014.2 | IESn, United Kingdom | IESn, United Kingdom | IES-VE/IES
LCEMo 3.10 | MLITp, Japan | TTEq, Japan | LCEM/MLIT-TTE
TRNSYS 17.01.0028 | TESSr/UWMs, United States | TESSr, United States | TRNSYS/TESS
a PSU: The Pennsylvania State University, United States
b UNO: University of Nebraska - Omaha, United States
c TAMU: Texas A&M University, United States
d NREL: National Renewable Energy Laboratory, United States
e JNA: J. Neymark & Associates, United States
f MDK: Mike D. Kennedy, Inc., United States
g DEEAP: Detailed Energy and Economic Analysis Program
h DeST: Designer's Simulation Toolkit
i LBNL: Lawrence Berkeley National Laboratory, United States
J JJH: James J. Hirsch & Associates, United States
k UC: University of California, United States
l DOE-BT: U.S. Department of Energy, Office of Building Technologies, Energy Efficiency and Renewable Energy, United States
m IES-VE: Integrated Environmental Solutions - Virtual Environment
n IES: Integrated Environmental Solutions, United Kingdom
o LCEM: Life Cycle Energy Management tool. LCEM results were only generated for the FC and SZ system cases (see Informative Annex B16,
Section B16.7.1); there are no LCEM results for the CV and VAV system cases (see Informative Annex B16, Section B16.7.2).
p MLIT: Ministry of Land, Infrastructure, Transportation and Tourism, Japan
q TTE: Takasago Thermal Engineering, Japan
r TESS: Thermal Energy System Specialists, United States
s UWM: University of Wisconsin - Madison, United States

## Table List
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.1
Example Results for Section 11, Airside HVAC BESTEST Cases AE101 through AE245
List of Tables
| Table | Description | Sheet Tab | Cell Range
| B16.7.1-1 | FC/SZ Heating Coil Load [QH] (kWh/h) | Tables 1 | A5–K17
| B16.7.1-2 | FC/SZ Total Cooling Coil Load [QCtotal] (kWh) |  | A20–K32
| B16.7.1-3 | FC/SZ Sensible Cooling Coil Load [QCsensible] (kWh/h) |  | A35–K47
| B16.7.1-4 | FC/SZ Latent Cooling Coil Load [QClatent] (kWh/h) |  | A50–K62
| B16.7.1-5 | FC/SZ Outdoor Air Temp (°C) |  | A65–K77
| B16.7.1-6 | FC/SZ Outdoor Air Humidity Ratio (%) |  | A80–K82
| B16.7.1-7 | FC/SZ Outdoor Air Mass Flow Rate (kgda/s) |  | A95–K107
| B16.7.1-8 | FC/SZ Cooling Coil Outlet Air Temperature (°C) |  | A110–K122
| B16.7.1-9 | FC/SZ Relative Humidity at Cooling Coil Outlet [RHcco] (%) |  | A125–K137
| B16.7.1-10 | FC/SZ Supply Fan Air Temperature Rise (°C) |  | A140–K152
| B16.7.1-11 | FC/SZ Supply Air Temperature (°C) |  | A155–K167
| B16.7.1-12 | FC/SZ Supply Air Humidity Ratio (g/gda) |  | A170–K182
| B16.7.1-13 | FC/SZ Supply Air Specific Volume (L/kgda) |  | A185–K197
| B16.7.1-14 | FC/SZ Supply Air Enthalpy (J/gda) |  | A200–K212
| B16.7.1-15 | FC/SZ Supply Air Mass Flow Rate (kgda/s) |  | A215–K227
| B16.7.1-16 | FC/SZ Outdoor Air Mass Flow to Supply Air Mass Flow Ratio (fraction) |  | A230–K242
| B16.7.1-17 | FC/SZ Zone Air Temperature (°C) |  | A245–K257
| B16.7.1-18 | FC/SZ Zone Humidity Ratio (g/gda) |  | A260–K272
| B16.7.1-19 | FC/SZ Moisture Added to Zone by Latent Gains (g/s) |  | A275–K288
| B16.7.1-20 | FC/SZ Return Fan Air Temperature Rise (°C) |  | A290–K299
| B16.7.1-21 | FC/SZ Delta Coil Load: SZ - FC (kWh/h) | Delta Tables 1 | A5–K12
| B16.7.1-22 | SZ Delta Coil Load: Economizer Operation (kWh/h) |  | A15–L23

## Figure List
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.1
Example Results for Section 11, Airside HVAC BESTEST Cases AE101 through AE245
List of Figures
| Figure | Description | Sheet Tab
| B16.7.1-1 | FC/SZ Heating Coil Load [QH] | Fig B16.7.1-1 HeatCoil
| B16.7.1-2 | FC/SZ Cooling Coil Load, Total [QCtotal] | Fig B16.7.1-2 CoolCoilTot
| B16.7.1-3 | FC/SZ Cooling Coil Load, Sensible [QCsensible] | Fig B16.7.1-3 CoolCoilSens
| B16.7.1-4 | FC/SZ Cooling Coil Load, Latent [QClatent] | Fig B16.7.1-4 CoolCoilLat
| B16.7.1-5 | FC/SZ Outdoor Air Temperature | Fig B16.7.1-5 OAT
| B16.7.1-6 | FC/SZ Outdoor Air Humidity Ratio | Fig B16.7.1-6 OAW
| B16.7.1-7 | FC/SZ Outdoor Air Mass Flow Rate | Fig B16.7.1-7 OAmassflow
| B16.7.1-8 | FC/SZ Cooling Coil Outlet Air Temperature | Fig B16.7.1-8 CCOT
| B16.7.1-9 | FC/SZ Cooling Coil Outlet Relative Humidity [RHcco] | Fig B16.7.1-9 RHcco
| B16.7.1-10 | FC/SZ Supply Fan Air Temperature Rise | Fig B16.7.1-10 Supply Fan dT
| B16.7.1-11 | FC/SZ Supply Air Temperature | Fig B16.7.1-11 SAT
| B16.7.1-12 | FC/SZ Supply Air Humidity Ratio | Fig B16.7.1-12 SAW
| B16.7.1-13 | FC/SZ Supply Air Specific Volume | Fig B16.7.1-13 SAVs
| B16.7.1-14 | FC/SZ Supply Air Enthalpy | Fig B16.7.1-14 SAenth
| B16.7.1-15 | FC/SZ Supply Air Mass Flow Rate | Fig B16.7.1-15 SAmassflow
| B16.7.1-16 | FC/SZ Outdoor Air to Supply Air Mass Flow Ratio | Fig B16.7.1-16 OAFrac
| B16.7.1-17 | FC/SZ Zone Air Temperature | Fig B16.7.1-17 ZoneAirT
| B16.7.1-18 | FC/SZ Zone Humidity Ratio | Fig B16.7.1-18 ZoneAirW
| B16.7.1-19 | FC/SZ Moisture Added to Zone by Latent Gains | Fig B16.7.1-19 Zone Lat Gain
| B16.7.1-20 | FC/SZ Return Fan Air Temperature Rise | Fig B16.7.1-20 Return Fan dT
| B16.7.1-21 | FC/SZ Delta Coil Load, SZ - FC | Fig B16.7.1-21 Delta SZ-FC
| B16.7.1-22 | FC/SZ Delta Coil Load, Economizer Operation | Fig B16.7.1-22 Delta Econo

## scrape titles new (hidden)
Org Tab Name | Org Chart Title | Org Yaxis Title | Proposed Num | New Tab Name | New Chart Title | New Axis Title
Fig 4.1-1 HeatCoil | Figure 4.1-1. FC/SZ Heating Coil Load [QH] | Coil Load (kWh/h) | 1 | Fig 4.1-1 HeatCoil | Figure 4.1-1. FC/SZ Heating Coil Load [QH] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.1-1 | FC/SZ Heating Coil Load [QH]
Fig 4.1-2 CoolCoilTot | Figure 4.1-2. FC/SZ Cooling Coil Load, Total [QCtotal] | Coil Load (kWh/h) | 2 | Fig 4.1-2 CoolCoilTot | Figure 4.1-2. FC/SZ Cooling Coil Load, Total [QCtotal] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.1-2 | FC/SZ Cooling Coil Load, Total [QCtotal]
Fig 4.1-3 CoolCoilSens | Figure 4.1-3. FC/SZ Cooling Coil Load, Sensible [QCsensible] | Coil Load (kWh/h) | 3 | Fig 4.1-3 CoolCoilSens | Figure 4.1-3. FC/SZ Cooling Coil Load, Sensible [QCsensible] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.1-3 | FC/SZ Cooling Coil Load, Sensible [QCsensible]
Fig 4.1-4 CoolCoilLat | Figure 4.1-4. FC/SZ Cooling Coil Load, Latent [QClatent] | Coil Load (kWh/h) | 4 | Fig 4.1-4 CoolCoilLat | Figure 4.1-4. FC/SZ Cooling Coil Load, Latent [QClatent] | Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.1-4 | FC/SZ Cooling Coil Load, Latent [QClatent]
Fig 4.1-5 OAT | Figure 4.1-5. FC/SZ Outdoor Air Temperature | Temperature (°C) | 5 | Fig 4.1-5 OAT | Figure 4.1-5. FC/SZ Outdoor Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.1-5 | FC/SZ Outdoor Air Temperature
Fig 4.1-6 OAW | Figure 4.1-6. FC/SZ Outdoor Air Humidity Ratio | Humidity Ratio (g/gda) | 6 | Fig 4.1-6 OAW | Figure 4.1-6. FC/SZ Outdoor Air Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.1-6 | FC/SZ Outdoor Air Humidity Ratio
Fig 4.1-7 OAmassflow | Figure 4.1-7. FC/SZ Outdoor Air Mass Flow Rate | Mass Flow Rate (kgda/s) | 7 | Fig 4.1-7 OAmassflow | Figure 4.1-7. FC/SZ Outdoor Air Mass Flow Rate | Mass Flow Rate (kgda/s) | TRUE | TRUE | TRUE | 4.1-7 | FC/SZ Outdoor Air Mass Flow Rate
Fig 4.1-8 CCOT | Figure 4.1-8. FC/SZ Cooling Coil Outlet Air Temperature | Temperature (°C) | 8 | Fig 4.1-8 CCOT | Figure 4.1-8. FC/SZ Cooling Coil Outlet Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.1-8 | FC/SZ Cooling Coil Outlet Air Temperature
Fig 4.1-9 RHcco | Figure 4.1-9. FC/SZ Cooling Coil Outlet Relative Humidity [RHcco] | Relative Humidity (%) | 9 | Fig 4.1-9 RHcco | Figure 4.1-9. FC/SZ Cooling Coil Outlet Relative Humidity [RHcco] | Relative Humidity (%) | TRUE | TRUE | TRUE | 4.1-9 | FC/SZ Cooling Coil Outlet Relative Humidity [RHcco]
Fig 4.1-10 Supply Fan dT | Figure 4.1-10. FC/SZ Supply Fan Air Temperature Rise | Temperature Rise (°C) | 10 | Fig 4.1-10 Supply Fan dT | Figure 4.1-10. FC/SZ Supply Fan Air Temperature Rise | Temperature Rise (°C) | TRUE | TRUE | TRUE | 4.1-10 | FC/SZ Supply Fan Air Temperature Rise
Fig 4.1-11 SAT | Figure 4.1-11. FC/SZ Supply Air Temperature | Temperature (°C) | 11 | Fig 4.1-11 SAT | Figure 4.1-11. FC/SZ Supply Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.1-11 | FC/SZ Supply Air Temperature
Fig 4.1-12 SAW | Figure 4.1-12. FC/SZ Supply Air Humidity Ratio | Humidity Ratio (g/gda) | 12 | Fig 4.1-12 SAW | Figure 4.1-12. FC/SZ Supply Air Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.1-12 | FC/SZ Supply Air Humidity Ratio
Fig 4.1-13 SAVs | Figure 4.1-13. FC/SZ Supply Air Specific Volume | Specific Volume (L/kgda) | 13 | Fig 4.1-13 SAVs | Figure 4.1-13. FC/SZ Supply Air Specific Volume | Specific Volume (L/kgda) | TRUE | TRUE | TRUE | 4.1-13 | FC/SZ Supply Air Specific Volume
Fig 4.1-14 SAenth | Figure 4.1-14. FC/SZ Supply Air Enthalpy | Enthalpy (J/gda) | 14 | Fig 4.1-14 SAenth | Figure 4.1-14. FC/SZ Supply Air Enthalpy | Enthalpy (J/gda) | TRUE | TRUE | TRUE | 4.1-14 | FC/SZ Supply Air Enthalpy
Fig 4.1-15 SAmassflow | Figure 4.1-15. FC/SZ Supply Air Mass Flow Rate | Mass Flow Rate (kgda/s) | 15 | Fig 4.1-15 SAmassflow | Figure 4.1-15. FC/SZ Supply Air Mass Flow Rate | Mass Flow Rate (kgda/s) | TRUE | TRUE | TRUE | 4.1-15 | FC/SZ Supply Air Mass Flow Rate
Fig 4.1-16 OAFrac | Figure 4.1-16. FC/SZ Outdoor Air to Supply Air Mass Flow Ratio | Ratio (0-1) | 16 | Fig 4.1-16 OAFrac | Figure 4.1-16. FC/SZ Outdoor Air to Supply Air Mass Flow Ratio | Ratio (0-1) | TRUE | TRUE | TRUE | 4.1-16 | FC/SZ Outdoor Air to Supply Air Mass Flow Ratio
Fig 4.1-17 ZoneAirT | Figure 4.1-17. FC/SZ Zone Air Temperature | Temperature (°C) | 17 | Fig 4.1-17 ZoneAirT | Figure 4.1-17. FC/SZ Zone Air Temperature | Temperature (°C) | TRUE | TRUE | TRUE | 4.1-17 | FC/SZ Zone Air Temperature
Fig 4.1-18 ZoneAirW | Figure 4.1-18. FC/SZ Zone Humidity Ratio | Humidity Ratio (g/gda) | 18 | Fig 4.1-18 ZoneAirW | Figure 4.1-18. FC/SZ Zone Humidity Ratio | Humidity Ratio (g/gda) | TRUE | TRUE | TRUE | 4.1-18 | FC/SZ Zone Humidity Ratio
Fig 4.1-19 Zone Lat Gain | Figure 4.1-19. FC/SZ Moisture Added to Zone by Latent Gains | Water Vapor (g/s) | 19 | Fig 4.1-19 Zone Lat Gain | Figure 4.1-19. FC/SZ Moisture Added to Zone by Latent Gains | Water Vapor (g/s) | TRUE | TRUE | TRUE | 4.1-19 | FC/SZ Moisture Added to Zone by Latent Gains
Fig 4.1-20 Return Fan dT | Figure 4.1-20. FC/SZ Return Fan Air Temperature Rise | Temperature Rise (°C) | 20 | Fig 4.1-20 Return Fan dT | Figure 4.1-20. FC/SZ Return Fan Air Temperature Rise | Temperature Rise (°C) | TRUE | TRUE | TRUE | 4.1-20 | FC/SZ Return Fan Air Temperature Rise
Fig 4.1-21 Delta SZ-FC | Figure 4.1-21. FC/SZ Delta Coil Load, SZ - FC | Delta Coil Load (kWh/h) | 21 | Fig 4.1-21 Delta SZ-FC | Figure 4.1-21. FC/SZ Delta Coil Load, SZ - FC | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.1-21 | FC/SZ Delta Coil Load, SZ - FC
Fig 4.1-22 Delta Econo | Figure 4.1-22. FC/SZ Delta Coil Load, Economizer Operation | Delta Coil Load (kWh/h) | 22 | Fig 4.1-22 Delta Econo | Figure 4.1-22. FC/SZ Delta Coil Load, Economizer Operation | Delta Coil Load (kWh/h) | TRUE | TRUE | TRUE | 4.1-22 | FC/SZ Delta Coil Load, Economizer Operation

## scrape titles (hidden)
Org Name | Yaxis Title | Proposed Num | New root | New Name | New Title | New Axis Title
HeatCoilkWh (2) | Heating Coil Load (Qh) (kWh/h) | 1 | HeatCoilkWh | Fig 4-1 HeatCoilkWh | Figure 4-1. Airside HVAC - FC/SZ: Heating Coil Load | Heating Coil Load (Qh) (kWh/h)
CoolCoilTot (2) | Cooling Coil Loads, Total (QCtotal) (kWh/h) | 2 | CoolCoilTot | Fig 4-2 CoolCoilTot | Figure 4-2. Airside HVAC - FC/SZ: Cooling Coil Loads, Total | Cooling Coil Loads, Total (QCtotal) (kWh/h)
CoolCoilSens (2) | Cooling Coil Loads, Sensible (QCsensible) (kWh/h) | 3 | CoolCoilSens | Fig 4-3 CoolCoilSens | Figure 4-3. Airside HVAC - FC/SZ: Cooling Coil Loads, Sensible | Cooling Coil Loads, Sensible (QCsensible) (kWh/h)
CoolCoilLat (2) | Cooling Coil Loads, Latent (QClatent) (kWh/h) | 4 | CoolCoilLat | Fig 4-4 CoolCoilLat | Figure 4-4. Airside HVAC - FC/SZ: Cooling Coil Loads, Latent | Cooling Coil Loads, Latent (QClatent) (kWh/h)
RHcco (2) | Cooling Coil Outlet Relative Humidity (RHcco) (%) | 5 | RHcco | Fig 4-5 RHcco | Figure 4-5. Airside HVAC - FC/SZ: Cooling Coil Outlet Relative Humidity | Cooling Coil Outlet Relative Humidity (RHcco) (%)
OAW (2) | Outdoor Air Humidity Ratio (g/gda) | 6 | OAW | Fig 4-6 OAW | Figure 4-6. Airside HVAC - FC/SZ: Outdoor Air Humidity Ratio | Outdoor Air Humidity Ratio (g/gda)
OAmassflow (2) | Outdoor Air Mass Flow Rate (kgda/s) | 7 | OAmassflow | Fig 4-7 OAmassflow | Figure 4-7. Airside HVAC - FC/SZ: Outdoor Air Mass Flow Rate | Outdoor Air Mass Flow Rate (kgda/s)
SAT (2) | Supply Air Temperature (°C) | 8 | SAT | Fig 4-8 SAT | Figure 4-8. Airside HVAC - FC/SZ: Supply Air Temperature | Supply Air Temperature (°C)
SAW (2) | Supply Air Humidity Ratio (g/gda) | 9 | SAW | Fig 4-9 SAW | Figure 4-9. Airside HVAC - FC/SZ: Supply Air Humidity Ratio | Supply Air Humidity Ratio (g/gda)
SAVs (2) | Supply Air Specific Volume (L/kgda) | 10 | SAVs | Fig 4-10 SAVs | Figure 4-10. Airside HVAC - FC/SZ: Supply Air Specific Volume | Supply Air Specific Volume (L/kgda)
SAenth (2) | Supply Air Enthalpy (j/gda) | 11 | SAenth | Fig 4-11 SAenth | Figure 4-11. Airside HVAC - FC/SZ: Supply Air Enthalpy | Supply Air Enthalpy (j/gda)
SAmassflow (2) | Supply Air Mass Flow Rate (kgda/s) | 12 | SAmassflow | Fig 4-12 SAmassflow | Figure 4-12. Airside HVAC - FC/SZ: Supply Air Mass Flow Rate | Supply Air Mass Flow Rate (kgda/s)
Supply Fan dT (2) | Supply Fan Temperature Rise (°C) | 13 | Supply Fan dT | Fig 4-13 Supply Fan dT | Figure 4-13. Airside HVAC - FC/SZ: Supply Fan Temperature Rise | Supply Fan Temperature Rise (°C)
ZoneAirT (2) | Zone Air Temperature (°C) | 14 | ZoneAirT | Fig 4-14 ZoneAirT | Figure 4-14. Airside HVAC - FC/SZ: Zone Air Temperature | Zone Air Temperature (°C)
Return Fan dT (2) | Return Fan Temperature Rise (°C) | 15 | Return Fan dT | Fig 4-15 Return Fan dT | Figure 4-15. Airside HVAC - FC/SZ: Return Fan Temperature Rise | Return Fan Temperature Rise (°C)
Delta SZ-FC (2) | Delta Coil Loads, SZ - FC ( | 16 | Delta SZ-FC | Fig 4-16 Delta SZ-FC | Figure 4-16. Airside HVAC - FC/SZ: Delta Coil Loads, SZ - FC | Delta Coil Loads (kWh/h), SZ - FC
Delta Econo (2) | Delta Coil Loads, SZ Econo - No Econo ( | 17 | Delta Econo | Fig 4-17 Delta Econo | Figure 4-17. Airside HVAC - FC/SZ: Delta Coil Loads, SZ Econo - No Econo | Delta Coil Loads (kWh/h), SZ Econo - No Econo

## scrape Table names (hidden)
worksheet | Table Name | sequence | Table Name Root | New Table Name | number
Tables 1 | Table 4.1-1. FC/SZ Heating Coil Load [QH] (kWh/h) | 1 | FC/SZ Heating Coil Load [QH] (kWh/h) | Table 4.1-1. FC/SZ Heating Coil Load [QH] (kWh/h) | 4.1-1 | TRUE
Tables 1 | Table 4.1-2. FC/SZ Total Cooling Coil Load [QCtotal] (kWh) | 2 | FC/SZ Total Cooling Coil Load [QCtotal] (kWh) | Table 4.1-2. FC/SZ Total Cooling Coil Load [QCtotal] (kWh) | 4.1-2 | TRUE
Tables 1 | Table 4.1-3. FC/SZ Sensible Cooling Coil Load [QCsensible] (kWh/h) | 3 | FC/SZ Sensible Cooling Coil Load [QCsensible] (kWh/h) | Table 4.1-3. FC/SZ Sensible Cooling Coil Load [QCsensible] (kWh/h) | 4.1-3 | TRUE
Tables 1 | Table 4.1-4. FC/SZ Latent Cooling Coil Load [QClatent] (kWh/h) | 4 | FC/SZ Latent Cooling Coil Load [QClatent] (kWh/h) | Table 4.1-4. FC/SZ Latent Cooling Coil Load [QClatent] (kWh/h) | 4.1-4 | TRUE
Tables 1 | Table 4.1-5. FC/SZ Outdoor Air Temp (°C) | 5 | FC/SZ Outdoor Air Temp (°C) | Table 4.1-5. FC/SZ Outdoor Air Temp (°C) | 4.1-5 | TRUE
Tables 1 | Table 4.1-6. FC/SZ Outdoor Air Humidity Ratio (%) | 6 | FC/SZ Outdoor Air Humidity Ratio (%) | Table 4.1-6. FC/SZ Outdoor Air Humidity Ratio (%) | 4.1-6 | TRUE
Tables 1 | Table 4.1-7. FC/SZ Outdoor Air Mass Flow Rate (kgda/s) | 7 | FC/SZ Outdoor Air Mass Flow Rate (kgda/s) | Table 4.1-7. FC/SZ Outdoor Air Mass Flow Rate (kgda/s) | 4.1-7 | TRUE
Tables 1 | Table 4.1-8. FC/SZ Cooling Coil Outlet Air Temperature (°C) | 8 | FC/SZ Cooling Coil Outlet Air Temperature (°C) | Table 4.1-8. FC/SZ Cooling Coil Outlet Air Temperature (°C) | 4.1-8 | TRUE
Tables 1 | Table 4.1-9. FC/SZ Relative Humidity at Cooling Coil Outlet [Rhcco] (%) | 9 | FC/SZ Relative Humidity at Cooling Coil Outlet [Rhcco] (%) | Table 4.1-9. FC/SZ Relative Humidity at Cooling Coil Outlet [Rhcco] (%) | 4.1-9 | TRUE
Tables 1 | Table 4.1-10. FC/SZ Supply Fan Air Temperature Rise (°C) | 10 | FC/SZ Supply Fan Air Temperature Rise (°C) | Table 4.1-10. FC/SZ Supply Fan Air Temperature Rise (°C) | 4.1-10 | TRUE
Tables 1 | Table 4.1-11. FC/SZ Supply Air Temperature (°C) | 11 | FC/SZ Supply Air Temperature (°C) | Table 4.1-11. FC/SZ Supply Air Temperature (°C) | 4.1-11 | TRUE
Tables 1 | Table 4.1-12. FC/SZ Supply Air Humidity Ratio (g/gda) | 12 | FC/SZ Supply Air Humidity Ratio (g/gda) | Table 4.1-12. FC/SZ Supply Air Humidity Ratio (g/gda) | 4.1-12 | TRUE
Tables 1 | Table 4.1-13. FC/SZ Supply Air Specific Volume (L/kgda) | 13 | FC/SZ Supply Air Specific Volume (L/kgda) | Table 4.1-13. FC/SZ Supply Air Specific Volume (L/kgda) | 4.1-13 | TRUE
Tables 1 | Table 4.1-14. FC/SZ Supply Air Enthalpy (j/gda) | 14 | FC/SZ Supply Air Enthalpy (j/gda) | Table 4.1-14. FC/SZ Supply Air Enthalpy (j/gda) | 4.1-14 | TRUE
Tables 1 | Table 4.1-15. FC/SZ Supply Air Mass Flow Rate (kgda/s) | 15 | FC/SZ Supply Air Mass Flow Rate (kgda/s) | Table 4.1-15. FC/SZ Supply Air Mass Flow Rate (kgda/s) | 4.1-15 | TRUE
Tables 1 | Table 4.1-16. FC/SZ Outdoor Air Mass Flow to Supply Air Mass Flow Ratio (fraction) | 16 | FC/SZ Outdoor Air Mass Flow to Supply Air Mass Flow Ratio (fraction) | Table 4.1-16. FC/SZ Outdoor Air Mass Flow to Supply Air Mass Flow Ratio (fraction) | 4.1-16 | TRUE
Tables 1 | Table 4.1-17. FC/SZ Zone Air Temperature (°C) | 17 | FC/SZ Zone Air Temperature (°C) | Table 4.1-17. FC/SZ Zone Air Temperature (°C) | 4.1-17 | TRUE
Tables 1 | Table 4.1-18. FC/SZ Zone Humidity Ratio (g/gda) | 18 | FC/SZ Zone Humidity Ratio (g/gda) | Table 4.1-18. FC/SZ Zone Humidity Ratio (g/gda) | 4.1-18 | TRUE
Tables 1 | Table 4.1-19. FC/SZ Moisture Added to Zone by Latent Gains (g/s) | 19 | FC/SZ Moisture Added to Zone by Latent Gains (g/s) | Table 4.1-19. FC/SZ Moisture Added to Zone by Latent Gains (g/s) | 4.1-19 | TRUE
Tables 1 | Table 4.1-20. FC/SZ Return Fan Air Temperature Rise (°C) | 20 | FC/SZ Return Fan Air Temperature Rise (°C) | Table 4.1-20. FC/SZ Return Fan Air Temperature Rise (°C) | 4.1-20 | TRUE
Delta Tables 1 | Table 4.1-21. FC/SZ Delta Coil Load: SZ - FC (kWh/h) | 21 | FC/SZ Delta Coil Load: SZ - FC (kWh/h) | Table 4.1-21. FC/SZ Delta Coil Load: SZ - FC (kWh/h) | 4.1-21 | TRUE
Delta Tables 1 | Table 4.1-22. SZ Delta Coil Load: Economizer Operation (kWh/h) | 22 | SZ Delta Coil Load: Economizer Operation (kWh/h) | Table 4.1-22. SZ Delta Coil Load: Economizer Operation (kWh/h) | 4.1-22 | TRUE

## Tables 1
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.1
Example Results for Section 11, Airside HVAC BESTEST Cases AE101 through AE245
Table B16.7.1-1. FC/SZ Heating Coil Load [QH] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 8.4195 | 8.4133 | 8.4521 | 8.7675 | 8.4534 | 8.513 | 8.3722 | 8.4159 | 8.5049
AE103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE201 | 8.3599 | 8.3488 | 8.3847 | 8.7092 | 8.387 | 8.446 | 8.3021 | 8.3563
AE203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Table B16.7.1-2. FC/SZ Total Cooling Coil Load [QCtotal] (kWh)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE103 | 0.78348 | 0.78407 | 0.7777 | 0.77693 | 0.76554 | 0.762 | 0.76262 | 0.78002 | 0.77201
AE104 | 5.5508 | 5.553 | 5.8358 | 5.5329 | 5.6728 | 5.607 | 5.6456 | 5.5475 | 5.6446
AE201 | 0 | 0 | 0 | 0 | 1.8464e-05 | 0 | 0 | 0
AE203 | 0.85614 | 0.85303 | 0.84533 | 0.84024 | 0.83269 | 0.83 | 0.83037 | 0.85249
AE204 | 5.6282 | 5.6234 | 5.8966 | 5.7114 | 5.7392 | 5.675 | 5.7133 | 5.6249
AE205 | 1.9163 | 1.9099 | 1.9287 | 1.9085 | 1.9127 | 1.915 | 1.911 | 1.9128
AE206 | 2.6768 | 2.6637 | 2.8181 | 2.7314 | 2.7383 | 2.696 | 2.6988 | 2.6709
AE226 | 3.3617 | 3.335 | 3.6428 | 3.4049 | 3.4182 | 3.377 | 3.3911 | 3.3553
AE245 | 2.2077 | 2.202 | 2.2158 | 2.1878 | 2.2073 | 2.21 | 2.2021 | 2.209
Table B16.7.1-3. FC/SZ Sensible Cooling Coil Load [QCsensible] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE103 | 0.78348 | 0.78407 | 0.7777 | 0.77693 | 0.76554 | 0.762 | 0.75229 | 0.78002 | 0.77201
AE104 | 3.4965 | 3.4882 | 3.5428 | 3.521 | 3.4986 | 3.48 | 3.3892 | 3.4932 | 3.4693
AE201 | 0 | 0 | 0 | 0 | 8.048e-08 | 0 | 0 | 0
AE203 | 0.85614 | 0.85303 | 0.84533 | 0.84024 | 0.83269 | 0.83 | 0.81912 | 0.85249
AE204 | 3.5739 | 3.5587 | 3.6078 | 3.5901 | 3.5657 | 3.547 | 3.4558 | 3.5705
AE205 | 1.9163 | 1.9099 | 1.9287 | 1.9085 | 1.9127 | 1.915 | 1.8799 | 1.9128
AE206 | 1.7064 | 1.7005 | 1.7314 | 1.7233 | 1.6967 | 1.695 | 1.6456 | 1.7033
AE226 | 1.5618 | 1.5568 | 1.593 | 1.5972 | 1.5548 | 1.552 | 1.5033 | 1.5603
AE245 | 2.2077 | 2.202 | 2.2158 | 2.1878 | 2.2073 | 2.21 | 2.1715 | 2.209
Table B16.7.1-4. FC/SZ Latent Cooling Coil Load [QClatent] (kWh/h)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AE103 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010332 | 0 | 0
AE104 | 2.0543 | 2.0648 | 2.293 | 2.0119 | 2.1742 | 2.127 | 2.2564 | 2.0544 | 2.1753
AE201 | 0 | 0 | 0 | 0 | 1.8383e-05 | 0 | 0 | 0
AE203 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01125 | 0
AE204 | 2.0543 | 2.0648 | 2.2888 | 2.1212 | 2.1735 | 2.128 | 2.2575 | 2.0544
AE205 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031088 | 0
AE206 | 0.97038 | 0.9632 | 1.0866 | 1.0082 | 1.0417 | 1 | 1.0532 | 0.96766
AE226 | 1.7999 | 1.7782 | 2.0498 | 1.8077 | 1.8634 | 1.825 | 1.8877 | 1.7951
AE245 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030615 | 0
Table B16.7.1-5. FC/SZ Outdoor Air Temp (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29
AE103 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
AE104 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
AE201 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29
AE203 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
AE204 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9
AE205 | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9
AE206 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AE226 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
AE245 | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9
Table B16.7.1-6. FC/SZ Outdoor Air Humidity Ratio (%)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00034449 | 0.00025893 | 0.00025893
AE103 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029339 | 0.0029359 | 0.0029317
AE104 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016761 | 0.016774 | 0.016766
AE201 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00034449 | 0.00025893
AE203 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029339 | 0.0029359
AE204 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016761 | 0.016774
AE205 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909
AE206 | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015546 | 0.015556
AE226 | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015546 | 0.015556
AE245 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909
Table B16.7.1-7. FC/SZ Outdoor Air Mass Flow Rate (kgda/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 0.11281 | 0.11283 | 0.11327 | 0.11954 | 0.11367 | 0.11327 | 0.11333 | 0.11281 | 0.11404
AE103 | 0.11149 | 0.11151 | 0.11327 | 0.11241 | 0.11367 | 0.11327 | 0.11327 | 0.11148 | 0.11139
AE104 | 0.11017 | 0.11019 | 0.11327 | 0.10928 | 0.11367 | 0.11327 | 0.11333 | 0.11017 | 0.11012
AE201 | 0.11281 | 0.11283 | 0.11327 | 0.1197 | 0.11367 | 0.11327 | 0.11327 | 0.11281
AE203 | 0.11149 | 0.11151 | 0.11327 | 0.11256 | 0.11367 | 0.11327 | 0.11327 | 0.11148
AE204 | 0.11017 | 0.11019 | 0.11327 | 0.10948 | 0.11367 | 0.11327 | 0.11327 | 0.11017
AE205 | 0.11121 | 0.11123 | 0.11327 | 0.11109 | 0.11367 | 0.11327 | 0.11327 | 0.11121
AE206 | 0.1099 | 0.10991 | 0.11327 | 0.10983 | 0.11367 | 0.11327 | 0.11327 | 0.1099
AE226 | 0.33551 | 0.33555 | 0.3398 | 0.32941 | 0.34102 | 0.3398 | 0.3398 | 0.3355
AE245 | 0.34027 | 0.34033 | 0.3398 | 0.33309 | 0.34102 | 0.3398 | 0.3398 | 0.34028
Table B16.7.1-8. FC/SZ Cooling Coil Outlet Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 29.3163 | 29.3262 | 29.0892 | 29.2222 | 29.0494 | 28.994 | 29.0359 | 29.309 | 29.702
AE103 | 18.5042 | 18.5 | 18.4621 | 19 | 18.5095 | 18.5195 | 18.5081 | 18.5094 | 18.5162
AE104 | 14.9386 | 14.9302 | 14.7013 | 15.2222 | 14.9265 | 14.8437 | 14.9194 | 14.9489 | 14.76
AE201 | 29.3163 | 29.3262 | 29.0892 | 28.6667 | 29.0498 | 28.9937 | 29.0359 | 29.309
AE203 | 18.5042 | 18.5 | 18.4622 | 18.4444 | 18.5093 | 18.5187 | 18.5081 | 18.5127
AE204 | 14.9386 | 14.9302 | 14.7219 | 14.6111 | 14.9264 | 14.8418 | 14.9194 | 14.949
AE205 | 18.506 | 18.5041 | 18.4632 | 18.4444 | 18.5236 | 18.5187 | 18.5198 | 18.5089
AE206 | 18.5142 | 18.5118 | 18.4552 | 18.4444 | 18.5888 | 18.5187 | 18.5759 | 18.5234
AE226 | 18.5142 | 18.5118 | 18.4446 | 18.4444 | 18.5897 | 18.5187 | 18.5759 | 18.52
AE245 | 18.5044 | 18.5025 | 18.4632 | 18.4444 | 18.5115 | 18.5187 | 18.5096 | 18.5
Table B16.7.1-9. FC/SZ Relative Humidity at Cooling Coil Outlet [RHcco] (%)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 6.3854 | 6.3813 |  | 6.4033 | 6.5151 | 6.75 | 6.8667 | 6.3531 | 6.2974
AE103 | 32.8432 | 32.5417 | 33.03 | 31.6536 | 32.5142 | 32.91 | 32.5498 | 32.8657 | 32.9843
AE104 | 100 | 99.9992 | 98.66 | 99.9615 | 99.6158 | 100 | 100 | 100 | 98.4538
AE201 | 6.3854 | 6.3813 |  | 6.6125 | 6.5149 | 6.75 | 6.8714 | 6.3531
AE203 | 32.8432 | 32.5417 | 33.03 | 32.7731 | 32.5148 | 32.91 | 32.5498 | 32.8591
AE204 | 100 | 99.9992 | 98.62 | 100 | 99.6397 | 100 | 100 | 100
AE205 | 44.5612 | 44.3101 | 44.81 | 44.8531 | 44.111 | 44.59 | 44.2027 | 44.5861
AE206 | 100 | 99.9992 | 99.36 | 99.9317 | 99.0255 | 100 | 100 | 100
AE226 | 100 | 99.9992 | 99.65 | 99.9317 | 99.8073 | 100 | 100 | 100
AE245 | 34.0915 | 33.8389 | 34.33 | 34.2864 | 33.9915 | 34.06 | 34.0684 | 34.1009
Table B16.7.1-10. FC/SZ Supply Fan Air Temperature Rise (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 0.60585 | 0.60658 | 0.5899 | 0 | 0.58614 | 0.5818 | 0.589 | 0.60572 | 0.61414
AE103 | 0.58381 | 0.58449 | 0.5899 | 0 | 0.58327 | 0.5818 | 0.589 | 0.58371 | 0.58791
AE104 | 0.57583 | 0.57646 | 0.5899 | 0 | 0.57663 | 0.5818 | 0.589 | 0.57574 | 0.58647
AE201 | 0.60585 | 0.60658 | 0.5899 |  | 0.58614 | 0.5818 | 0.589 | 0.60572
AE203 | 0.58381 | 0.58449 | 0.5899 |  | 0.58327 | 0.5818 | 0.589 | 0.58372
AE204 | 0.57583 | 0.57646 | 0.5899 |  | 0.57663 | 0.5818 | 0.589 | 0.57574
AE205 | 0.5836 | 0.58428 | 0.5899 |  | 0.58162 | 0.5818 | 0.589 | 0.5835
AE206 | 0.58261 | 0.58329 | 0.5899 |  | 0.57377 | 0.5818 | 0.589 | 0.5825
AE226 | 0.58261 | 0.58329 | 0.5899 |  | 0.57366 | 0.5818 | 0.589 | 0.5825
AE245 | 0.58379 | 0.58632 | 0.5899 |  | 0.58306 | 0.5818 | 0.589 | 0.58367
Table B16.7.1-11. FC/SZ Supply Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 29.9222 | 29.9328 | 29.6791 | 29.2222 | 29.6355 | 29.5758 | 29.6249 | 29.9147 | 30.3161
AE103 | 19.088 | 19.0845 | 19.052 | 19 | 19.0928 | 19.1013 | 19.0971 | 19.0931 | 19.1041
AE104 | 15.5144 | 15.5066 | 15.2912 | 15.2222 | 15.5032 | 15.4255 | 15.5084 | 15.5247 | 15.3465
AE201 | 29.9222 | 29.9328 | 29.6791 |  | 29.6359 | 29.5755 | 29.6249 | 29.9147
AE203 | 19.088 | 19.0845 | 19.0521 |  | 19.0925 | 19.1005 | 19.0971 | 19.0964
AE204 | 15.5144 | 15.5066 | 15.3118 |  | 15.5031 | 15.4236 | 15.5084 | 15.5247
AE205 | 19.0896 | 19.0883 | 19.0531 |  | 19.1052 | 19.1005 | 19.1088 | 19.0924
AE206 | 19.0968 | 19.0951 | 19.0451 |  | 19.1626 | 19.1005 | 19.1649 | 19.1059
AE226 | 19.0968 | 19.0951 | 19.0345 |  | 19.1634 | 19.1005 | 19.1649 | 19.1025
AE245 | 19.0882 | 19.0888 | 19.0531 |  | 19.0946 | 19.1005 | 19.0986 | 19.0837
Table B16.7.1-12. FC/SZ Supply Air Humidity Ratio (g/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 0.0016041 | 0.0016042 | 0.0016416 | 0.0016 | 0.0016122 | 0.00167 | 0.0016965 | 0.0015953 | 0.0016176
AE103 | 0.0043252 | 0.0042844 | 0.0043367 | 0.0043 | 0.0042844 | 0.004355 | 0.004285 | 0.0043297 | 0.0043473
AE104 | 0.010605 | 0.010599 | 0.010296 | 0.0108 | 0.010558 | 0.010581 | 0.010585 | 0.010612 | 0.010316
AE201 | 0.0016041 | 0.0016041 | 0.0016416 | 0.0016 | 0.0016122 | 0.00167 | 0.0016977 | 0.0015953
AE203 | 0.0043252 | 0.0042845 | 0.0043367 | 0.0043 | 0.0042844 | 0.004355 | 0.004285 | 0.0043297
AE204 | 0.010605 | 0.0106 | 0.010306 | 0.0104 | 0.010561 | 0.01058 | 0.010585 | 0.010612
AE205 | 0.0058837 | 0.00585 | 0.0059 | 0.0059 | 0.005832 | 0.005916 | 0.0058378 | 0.0058881
AE206 | 0.013368 | 0.013367 | 0.013227 | 0.0133 | 0.013302 | 0.013424 | 0.013413 | 0.013376
AE226 | 0.013368 | 0.013367 | 0.013257 | 0.0133 | 0.01341 | 0.013424 | 0.013413 | 0.013373
AE245 | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909
Table B16.7.1-13. FC/SZ Supply Air Specific Volume (L/kgda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 860.7762 | 860.6945 | 833.33 |  | 830.3519 |  | 833 | 856.5396 | 861.9203
AE103 | 833.6275 | 833.4546 | 833.33 |  | 830.3519 |  | 833 | 829.5769 | 833.7092
AE104 | 831.6898 | 831.5517 | 833.33 |  | 830.3519 |  | 833 | 827.6673 | 830.8336
AE201 | 860.7762 | 860.6945 | 833.33 |  | 830.3519 |  | 833 | 856.5396
AE203 | 833.6275 | 833.4546 | 833.33 |  | 830.3519 |  | 833 | 829.5862
AE204 | 831.6898 | 831.5517 | 833.33 |  | 830.3519 |  | 833 | 827.6674
AE205 | 835.7063 | 835.549 | 833.33 |  | 830.3519 |  | 833 | 831.6391
AE206 | 845.6895 | 845.5719 | 833.33 |  | 830.3519 |  | 833 | 841.5963
AE226 | 845.6895 | 845.5719 | 833.33 |  | 830.3519 |  | 833 | 841.5827
AE245 | 833.8485 | 833.6965 | 833.33 |  | 830.3519 |  | 833 | 829.7636
Table B16.7.1-14. FC/SZ Supply Air Enthalpy (J/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 34.2029 |  | 34.02 |  | 33.8997 |  | 34.1363 | 34.1729 | 34.6348
AE103 | 30.1736 |  | 30.14 |  | 30.0522 |  | 30.0761 | 30.1899 | 30.2457
AE104 | 42.4358 |  | 41.4 |  | 42.2878 |  | 42.3718 | 42.4646 | 41.5345
AE201 | 34.2055 |  | 34.02 |  | 33.9001 |  | 34.1393 | 34.1729
AE203 | 30.1752 |  | 30.14 |  | 30.0519 |  | 30.0761 | 30.1932
AE204 | 42.4371 |  | 41.44 |  | 42.2941 |  | 42.3718 | 42.4647
AE205 | 34.1298 |  | 34.1 |  | 33.9902 |  | 34.0251 | 34.1421
AE206 | 53.121 |  | 52.67 |  | 52.9973 |  | 53.29 | 53.1486
AE226 | 53.121 |  | 52.74 |  | 53.2723 |  | 53.29 | 53.1378
AE245 | 30.5955 |  | 30.58 |  | 30.5528 |  | 30.5893 | 30.5893
Table B16.7.1-15. FC/SZ Supply Air Mass Flow Rate (kgda/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 0.32963 | 0.32966 | 0.3398 | 0.35862 | 0.34102 | 0.3398 | 0.3398 | 0.32964 | 0.32961
AE103 | 0.34036 | 0.34043 | 0.3398 | 0.33724 | 0.34102 | 0.3398 | 0.3398 | 0.34035 | 0.34034
AE104 | 0.34115 | 0.34121 | 0.3398 | 0.32785 | 0.34102 | 0.3398 | 0.3398 | 0.34114 | 0.34145
AE201 | 0.32963 | 0.32966 | 0.3398 | 0.35909 | 0.34102 | 0.3398 | 0.3398 | 0.32964
AE203 | 0.34036 | 0.34043 | 0.3398 | 0.33768 | 0.34102 | 0.3398 | 0.3398 | 0.34035
AE204 | 0.34115 | 0.34121 | 0.3398 | 0.32843 | 0.34102 | 0.3398 | 0.3398 | 0.34114
AE205 | 0.33952 | 0.33958 | 0.3398 | 0.33327 | 0.34102 | 0.3398 | 0.3398 | 0.33951
AE206 | 0.33551 | 0.33555 | 0.3398 | 0.32948 | 0.34102 | 0.3398 | 0.3398 | 0.33549
AE226 | 0.33551 | 0.33555 | 0.3398 | 0.32941 | 0.34102 | 0.3398 | 0.3398 | 0.3355
AE245 | 0.34027 | 0.34033 | 0.3398 | 0.33309 | 0.34102 | 0.3398 | 0.3398 | 0.34028
Table B16.7.1-16. FC/SZ Outdoor Air Mass Flow to Supply Air Mass Flow Ratio (fraction)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 0.34224 | 0.34226 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33353 | 0.34223 | 0.34597
AE103 | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | 0.3273
AE104 | 0.32294 | 0.32294 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33353 | 0.32295 | 0.32252
AE201 | 0.34224 | 0.34226 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.34223
AE203 | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756
AE204 | 0.32294 | 0.32294 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32295
AE205 | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756
AE206 | 0.32756 | 0.32756 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32757
AE226 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
AE245 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Table B16.7.1-17. FC/SZ Zone Air Temperature (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 21.1111 | 21.1111 | 21.0991 | 21.1111 | 21.1183 | 21.111 | 21.111 | 21.1138 | 21.111
AE103 | 23.3333 | 23.3333 | 23.3479 | 23.3333 | 23.3293 | 23.3321 | 23.333 | 23.3325 | 23.333
AE104 | 23.8889 | 23.8889 | 23.8764 | 23.8889 | 23.8823 | 23.8901 | 23.889 | 23.8905 | 23.889
AE201 | 21.1111 | 21.1111 | 21.099 | 21.1111 | 21.1187 | 21.1107 | 21.111 | 21.1138
AE203 | 23.3333 | 23.3333 | 23.3481 | 23.3333 | 23.3288 | 23.3313 | 23.333 | 23.3358
AE204 | 23.8889 | 23.8889 | 23.897 | 23.8889 | 23.8822 | 23.8882 | 23.889 | 23.8905
AE205 | 23.3333 | 23.3333 | 23.3479 | 23.3333 | 23.3296 | 23.3313 | 23.333 | 23.3302
AE206 | 23.3333 | 23.3333 | 23.3378 | 23.3333 | 23.33 | 23.3313 | 23.333 | 23.3365
AE226 | 23.3333 | 23.3333 | 23.3272 | 23.3333 | 23.33 | 23.3313 | 23.333 | 23.3331
AE245 | 23.3333 | 23.3333 | 23.3479 | 23.3333 | 23.3294 | 23.3313 | 23.333 | 23.3227
Table B16.7.1-18. FC/SZ Zone Humidity Ratio (g/gda)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 0.002304 | 0.0023041 | 0.0023324 | 0.0022 | 0.0022887 | 0.00237 | 0.0023731 | 0.0022906 | 0.0023363
AE103 | 0.005002 | 0.0049611 | 0.0050311 | 0.005 | 0.0049599 | 0.005059 | 0.0049605 | 0.0050086 | 0.0050353
AE104 | 0.01128 | 0.011274 | 0.010986 | 0.0115 | 0.011233 | 0.011285 | 0.011261 | 0.011291 | 0.011004
AE201 | 0.002304 | 0.0023041 | 0.0023324 | 0.0022 | 0.0022887 | 0.002374 | 0.0023743 | 0.0022906
AE203 | 0.005002 | 0.0049611 | 0.0050311 | 0.005 | 0.0049599 | 0.005059 | 0.0049605 | 0.0050086
AE204 | 0.01128 | 0.011274 | 0.010995 | 0.0111 | 0.011236 | 0.011284 | 0.011261 | 0.011291
AE205 | 0.0065621 | 0.0065284 | 0.0065931 | 0.0066 | 0.0065075 | 0.00662 | 0.0065133 | 0.0065687
AE206 | 0.014054 | 0.014053 | 0.013921 | 0.014 | 0.013978 | 0.014128 | 0.014089 | 0.014065
AE226 | 0.014054 | 0.014053 | 0.013951 | 0.0141 | 0.014086 | 0.014128 | 0.014089 | 0.014062
AE245 | 0.0051678 | 0.005134 | 0.0052044 | 0.0052 | 0.0051565 | 0.005212 | 0.0051623 | 0.00517
Table B16.7.1-19. FC/SZ Moisture Added to Zone by Latent Gains (g/s)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE101 | 0.23072 | 0.23072 | 0.23474 | 0.21517 | 0.23073 | 0.23786 | 0.22991 | 0.22921 | 0.23689
AE103 | 0.23034 | 0.23034 | 0.23595 | 0.23607 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | 0.23415
AE104 | 0.23025 | 0.23026 | 0.23437 | 0.2295 | 0.23026 | 0.23922 | 0.22945 | 0.23169 | 0.23471
AE201 | 0.23072 | 0.23075 | 0.23474 | 0.21546 | 0.23073 | 0.23922 | 0.22991 | 0.22921
AE203 | 0.23034 | 0.23032 | 0.23595 | 0.23638 | 0.23036 | 0.23922 | 0.22954 | 0.23107
AE204 | 0.23025 | 0.23025 | 0.23437 | 0.2299 | 0.23026 | 0.23922 | 0.22945 | 0.23169
AE205 | 0.23034 | 0.23035 | 0.23551 | 0.23329 | 0.23036 | 0.23922 | 0.22954 | 0.23107
AE206 | 0.23034 | 0.23035 | 0.23595 | 0.23064 | 0.23036 | 0.23922 | 0.22954 | 0.23107
AE226 | 0.23034 | 0.23035 | 0.23595 | 0.26353 | 0.23036 | 0.23922 | 0.22954 | 0.23107
AE245 | 0.23034 | 0.23035 | 0.23595 | 0.23316 | 0.23036 | 0.23922 | 0.22954 | 0.23108
[(Zone Supply Air Mass Flow) × {(Zone Humidity Ratio) – (Zone Supply Air Humidity Ratio )} × 1000 g/kg]
Table B16.7.1-20. FC/SZ Return Fan Air Temperature Rise (°C)
| QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE201 | 0.27209 | 0.295 | 0.29495 | 0.27778 | 0.28973 | 0.2909 | 0.295 | 0.27201
AE203 | 0.31262 | 0.29704 | 0.29495 | 0.27778 | 0.29127 | 0.2909 | 0.295 | 0.31247
AE204 | 0.32615 | 0.29715 | 0.29495 | 0.27778 | 0.28796 | 0.2909 | 0.295 | 0.326
AE205 | 0.3125 | 0.29693 | 0.29495 | 0.33333 | 0.29045 | 0.2909 | 0.295 | 0.31234
AE206 | 0.31193 | 0.29641 | 0.29495 | 0.27778 | 0.28654 | 0.2909 | 0.295 | 0.31178
AE226 | 0.31193 | 0.29641 | 0.29495 | 0.33333 | 0.28648 | 0.2909 | 0.295 | 0.31179
AE245 | 0.3126 | 0.29703 | 0.29495 | 0.33333 | 0.29117 | 0.2909 | 0.295 | 0.31245

## Delta Tables 1
ASHRAE Standard 140-2023, Informative Annex B16, Section B16.7.1
Example Results for Section 11, Airside HVAC BESTEST Cases AE101 through AE245
Table B16.7.1-21. FC/SZ Delta Coil Load: SZ - FC (kWh/h)
|  | QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | Load | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE201-AE101 | Heating | -0.059605 | -0.064549 | -0.067382 | -0.058321 | -0.066421 | -0.067 | -0.070108 | -0.059584
AE203-AE103 | Sensible Cooling | 0.072652 | 0.068956 | 0.067631 | 0.063303 | 0.067154 | 0.068 | 0.067746 | 0.072468
AE204-AE104 | Total Cooling | 0.077372 | 0.07042 | 0.06085 | 0.17848 | 0.066443 | 0.068 | 0.067691 | 0.077318
| Sensible Cooling | 0.077372 | 0.07042 | 0.06503 | 0.069165 | 0.067164 | 0.067 | 0.066631 | 0.077323
| Latent Cooling | 0 | -5.7732e-15 | -0.0041804 | 0.10932 | -0.00072059 | 0.001 | 0.0010596 | -5.7975e-06
Table B16.7.1-22. SZ Delta Coil Load: Economizer Operation (kWh/h)
|  | QAS | DEEAP | DeST | DOE-2.2 | EnergyPlus | IES-VE | LCEM | TRNSYS | OpenSimula
Test Case | Load | PSU-TAMU-NREL | AAON | TsinghuaU-LBNL | NREL | GARD | IES | MLIT-TTE | TESS | US
AE245-AE205 | Total Cooling | 0.2914 | 0.29211 | 0.28703 | 0.2793 | 0.29465 | 0.295 | 0.29113 | 0.29622
| Sensible Cooling | 0.2914 | 0.29211 | 0.28703 | 0.2793 | 0.29465 | 0.295 | 0.29161 | 0.29622
| Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | -0.00047276 | 0
AE226-AE206 | Total Cooling | 0.68493 | 0.67125 | 0.82473 | 0.67348 | 0.67988 | 0.681 | 0.69228 | 0.68443
| Sensible Cooling | -0.14458 | -0.14373 | -0.13841 | -0.12602 | -0.14185 | -0.143 | -0.14226 | -0.143
| Latent Cooling | 0.82951 | 0.81497 | 0.96314 | 0.7995 | 0.82172 | 0.825 | 0.83454 | 0.82743

## Detailed Location Results
User-definable chart to look at diagnostic results. Allows selection of test case and diagnostic variable; see Cells B4, B5 (instructions in Cells C4, C5). Displays selected case and diagnostic value for all programs by system location. For selection of viewed program results, see Cells A8-A20, A42-A54 (instructions in Cell A4).
Output spreadsheet for Airside HVAC BESTEST
Aggregator Sheet - Detailed Location Results
| AE101 | <== Select Case | Desc: | AE101: FC, Heating, OD/OWB = -29.00/-29.00 °C
| Dry Bulb Temperature (°C) | <== Select Variable | Title | AE101: FC, Heating, OD/OWB = -29.00/-29.00 °C Dry Bulb Temperature (°C)
InOut | Tab Name | [13 empty] | Dry Bulb Temperature (°C) | 1
1 | QAS | [11 empty] | OFFSETS |  | Humidity Ratio (g/gda) | 2
1 | DEEAP | [13 empty] | Specific Volume (L/kgda) | 3
1 | DeST | [13 empty] | Enthalpy (J/gda) | 4
1 | DOE22 | [11 empty] | Summary Outputs | Detailed Outputs | Mass Flow Rate (kgda/s) | 5
1 | EPlus | [10 empty] | AE101 | 1 | 1
1 | IES-VE | [10 empty] | AE103 | 2 | 6
1 | LCEM | [10 empty] | AE104 | 3 | 11
1 | TRNSYS | [10 empty] | AE201 | 29 | 29
0 | YourData | [10 empty] | AE203 | 30 | 34
0 | Blank | [10 empty] | AE204 | 31 | 39
0 | Blank | [10 empty] | AE205 | 32 | 44
0 | Blank | [10 empty] | AE206 | 33 | 49
0 | Blank | [10 empty] | AE226 | 34 | 54
[12 empty] | AE245 | 35 | 59
Table Below
*
*
*
*
\/
|  |  | Results Offset ==> | 1 | Results Row ==> | 1 |  | Result Sets ==> | #N/A | Ret Fan Exists | FALSE
| Result Col Offset==> | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| Air Loop Location==> | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone
| Air Loop Location==> | Air | Air | Outlet | Outlet | Air | Air
InOut | Tab Name | Outdoor Air | Mixed Air | Heat Coil Outlet | Cool Coil Outlet | Supply Air | Zone Air | Return Air
1 | QAS | -29 | 4.0034 | 29.3163 | 29.3163 | 29.9222 | 21.1111 | 21.1111 | #N/A
1 | DEEAP | -29 | 4.0029 | 29.3262 | 29.3262 | 29.9328 | 21.1111 | #N/A | #N/A
1 | DeST | -29 | 4.4073 | 29.0892 | 29.0892 | 29.6791 | 21.0991 | 21.0991 | #N/A
1 | DOE22 | -29 | 4.3889 | 29.2222 | 29.2222 | 29.2222 | 21.1111 | 21.1111 | #N/A
1 | EPlus | -29 | 4.4539 | 29.0494 | 29.0494 | 29.6355 | 21.1183 | 21.1183 | #N/A
1 | IES-VE | -29 | 4.4073 | 28.994 | 28.994 | 29.5758 | 21.111 | 21.111 | #N/A
1 | LCEM | -29 | 4.3977 | 29.0359 | 29.0359 | 29.6249 | 21.111 | 21.111 | #N/A
1 | TRNSYS | -29 | 4.0054 | 29.309 | 29.309 | 29.9147 | 21.1138 | 21.1138 | #N/A
0 | YourData | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | Blank | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Note on A5: Set to 0 to turn off result set.

## Aggregate Results
Output spreadsheet for Airside HVAC BESTEST
0
Aggregator Sheet - Collects data from Plots
Cooling Coil Outlet Relative Humidity (RHcco) (%) |  | Results Column ==> | 8
OFFSETS
Cells B9:N9 contain the tab name of the results set. By changing the tab name all results for that column are changed and plot data updated. It is possible to change the order or plot multiple new results sets by changing the tab names. Plots currently only address through column J. To plot more than 9 results sets the plot ranges must be adjusted.
Tab Name==> | QAS | DEEAP | DeST | DOE22 | EPlus | IES-VE | LCEM | TRNSYS | YourData | Blank | Blank | Blank | Blank |  | Summary Outputs | Detailed Outputs |  |  | Summary Output Columns | Detailed Output Columns
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 6.3854 | 6.3813 | #N/A | 6.4033 | 6.5151 | 6.75 | 6.8667 | 6.3531 | 6.2974 | #N/A | #N/A | #N/A | #N/A | AE101 | 1 | 1 | FC Heat | AE101: FC, Heating, OD/OWB = -29.00/-29.00 °C | Zone Sensible Heating Load (QZHsensible) (kWh) | Outdoor Air (oa)
AE103 FC Dry Coil 15.5/-3.0 | 32.8432 | 32.5417 | 33.03 | 31.6536 | 32.5142 | 32.91 | 32.5498 | 32.8657 | 32.9843 | #N/A | #N/A | #N/A | #N/A | AE103 | 2 | 6 | FC Dry Coil | AE103: FC, Dry Coil Cooling, OD/OWB = 15.50/7.21 °C | Zone Sensible Cooling Load (QZCsensible) (kWh) | Mixed Air (ma)
AE104 FC Wet Coil 26.9/22.1 | 100 | 99.9992 | 98.66 | 99.9615 | 99.6158 | 100 | 100 | 100 | 98.4538 | #N/A | #N/A | #N/A | #N/A | AE104 | 3 | 11 | FC Wet Coil | AE104: FC, Wet Coil Cooling, OD/OWB = 26.90/23.44 °C | Zone Latent Load (QZlatent) (kWh) | Heat Coil Outlet (hco)
AE201 SZ Heat -29.0/-29.0 | 6.3854 | 6.3813 | #N/A | 6.6125 | 6.5149 | 6.75 | 6.8714 | 6.3531 | #N/A | #N/A | #N/A | #N/A | #N/A | AE201 | 29 | 29 | SZ Heat | AE201: FC, Heating, -OD/OWB = 29.00/-29.00 °C | Heating Coil Load (Qh) (kWh) | Cool Coil Outlet (cco)
AE203 SZ Dry Coil 15.5/-3.0 | 32.8432 | 32.5417 | 33.03 | 32.7731 | 32.5148 | 32.91 | 32.5498 | 32.8591 | #N/A | #N/A | #N/A | #N/A | #N/A | AE203 | 30 | 34 | SZ Dry Coil | AE203: SZ, Dry Coil Cooling, OD/OWB = 15.50/7.21 °C | Cooling Coil Loads - Sensible (Qcsensible) (kWh) | Supply Air (sa)
AE204 SZ Wet Coil 26.9/22.1 | 100 | 99.9992 | 98.62 | 100 | 99.6397 | 100 | 100 | 100 | #N/A | #N/A | #N/A | #N/A | #N/A | AE204 | 31 | 39 | SZ Wet Coil | AE204: SZ, Wet Coil Cooling, OD/OWB = 26.90/23.44 °C | Cooling Coil Loads - Latent (Qclatent) (kWh) | Zone Ar (z1)
AE205 SZ Dry Coil 24.9/2.4 No Econo | 44.5612 | 44.3101 | 44.81 | 44.8531 | 44.111 | 44.59 | 44.2027 | 44.5861 | #N/A | #N/A | #N/A | #N/A | #N/A | AE205 | 32 | 44 | SZ Dry Coil 2, No Econo | AE205: SZ, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, No Economizer | Cooling Coil Loads - Total (Qctotal) (kWh)
AE206 SZ Wet Coil 23.0/20.9 No Econo | 100 | 99.9992 | 99.36 | 99.9317 | 99.0255 | 100 | 100 | 100 | #N/A | #N/A | #N/A | #N/A | #N/A | AE206 | 33 | 49 | SZ Wet Coil 2, No Econo | AE206: SZ, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, No Economizer | Cooling Coil Outlet Relative Humidity (RHcco) (%)
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 100 | 99.9992 | 99.65 | 99.9317 | 99.8073 | 100 | 100 | 100 | #N/A | #N/A | #N/A | #N/A | #N/A | AE226 | 34 | 54 | SZ Dry Coil 2, Dry Bulb Econo | AE226: SZ, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, Dry Bulb Econo.
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 34.0915 | 33.8389 | 34.33 | 34.2864 | 33.9915 | 34.06 | 34.0684 | 34.1009 | #N/A | #N/A | #N/A | #N/A | #N/A | AE245 | 35 | 59 | SZ Wet Coil 2, Enthalpy Econo | AE245: SZ, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, Enthalpy Econo
Heating Coil Load (Qh) (kWh) |  | Results Column ==> | 4
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 8.4195 | 8.4133 | 8.4521 | 8.7675 | 8.4534 | 8.513 | 8.3722 | 8.4159 | 8.5049 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 8.3599 | 8.3488 | 8.3847 | 8.7092 | 8.387 | 8.446 | 8.3021 | 8.3563 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads - Sensible (Qcsensible) (kWh) |  | Results Column ==> | 5
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.78348 | 0.78407 | 0.7777 | 0.77693 | 0.76554 | 0.762 | 0.75229 | 0.78002 | 0.77201 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 3.4965 | 3.4882 | 3.5428 | 3.521 | 3.4986 | 3.48 | 3.3892 | 3.4932 | 3.4693 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 8.048e-08 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.85614 | 0.85303 | 0.84533 | 0.84024 | 0.83269 | 0.83 | 0.81912 | 0.85249 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 3.5739 | 3.5587 | 3.6078 | 3.5901 | 3.5657 | 3.547 | 3.4558 | 3.5705 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 1.9163 | 1.9099 | 1.9287 | 1.9085 | 1.9127 | 1.915 | 1.8799 | 1.9128 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 1.7064 | 1.7005 | 1.7314 | 1.7233 | 1.6967 | 1.695 | 1.6456 | 1.7033 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 1.5618 | 1.5568 | 1.593 | 1.5972 | 1.5548 | 1.552 | 1.5033 | 1.5603 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 2.2077 | 2.202 | 2.2158 | 2.1878 | 2.2073 | 2.21 | 2.1715 | 2.209 | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads - Latent (Qclatent) (kWh) |  | Results Column ==> | 6
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010332 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 2.0543 | 2.0648 | 2.293 | 2.0119 | 2.1742 | 2.127 | 2.2564 | 2.0544 | 2.1753 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 1.8383e-05 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01125 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 2.0543 | 2.0648 | 2.2888 | 2.1212 | 2.1735 | 2.128 | 2.2575 | 2.0544 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0.031088 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.97038 | 0.9632 | 1.0866 | 1.0082 | 1.0417 | 1 | 1.0532 | 0.96766 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 1.7999 | 1.7782 | 2.0498 | 1.8077 | 1.8634 | 1.825 | 1.8877 | 1.7951 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0 | 0 | 0 | 0 | 0 | 0 | 0.030615 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Loads - Total (Qctotal) (kWh) |  | Results Column ==> | 7
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.78348 | 0.78407 | 0.7777 | 0.77693 | 0.76554 | 0.762 | 0.76262 | 0.78002 | 0.77201 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 5.5508 | 5.553 | 5.8358 | 5.5329 | 5.6728 | 5.607 | 5.6456 | 5.5475 | 5.6446 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0 | 0 | 0 | 0 | 1.8464e-05 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.85614 | 0.85303 | 0.84533 | 0.84024 | 0.83269 | 0.83 | 0.83037 | 0.85249 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 5.6282 | 5.6234 | 5.8966 | 5.7114 | 5.7392 | 5.675 | 5.7133 | 5.6249 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 1.9163 | 1.9099 | 1.9287 | 1.9085 | 1.9127 | 1.915 | 1.911 | 1.9128 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 2.6768 | 2.6637 | 2.8181 | 2.7314 | 2.7383 | 2.696 | 2.6988 | 2.6709 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 3.3617 | 3.335 | 3.6428 | 3.4049 | 3.4182 | 3.377 | 3.3911 | 3.3553 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 2.2077 | 2.202 | 2.2158 | 2.1878 | 2.2073 | 2.21 | 2.2021 | 2.209 | #N/A | #N/A | #N/A | #N/A | #N/A
Detailed Outputs
Outdoor Air Temp |  | Results Column ==> | 1 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Temperature (just for 5 cases)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE201 SZ Heat -29.0/-29.0 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | -29 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 26.9 | 26.8889 | 26.9 | 26.8889 | 26.9 | 26.9 | 26.9 | 26.9 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 24.9 | 24.8889 | 24.9 | 24.8889 | 24.9 | 24.9 | 24.9 | 24.9 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Humidity Ratio |  | Results Column ==> | 1 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00034449 | 0.00025893 | 0.00025893 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029339 | 0.0029359 | 0.0029317 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016761 | 0.016774 | 0.016766 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00034449 | 0.00025893 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029339 | 0.0029359 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016761 | 0.016774 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015546 | 0.015556 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015546 | 0.015556 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909 | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Humidity Ratio (just for 5 cases)
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE201 SZ Heat -29.0/-29.0 | 0.00025893 | 0.00025894 | 0.00026 | 0.0003 | 0.00025901 | 0.000262 | 0.00034449 | 0.00025893 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.0029359 | 0.0028954 | 0.002948 | 0.0029 | 0.0029334 | 0.002947 | 0.0029339 | 0.0029359 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.016774 | 0.016783 | 0.01685 | 0.0168 | 0.016772 | 0.016839 | 0.016761 | 0.016774 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.015556 | 0.015523 | 0.01563 | 0.0156 | 0.015565 | 0.015616 | 0.015546 | 0.015556 | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Mass Flow Rat |  | Results Column ==> | 1 |  | Results Row Offset==> | 4
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.11281 | 0.11283 | 0.11327 | 0.11954 | 0.11367 | 0.11327 | 0.11333 | 0.11281 | 0.11404 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.11149 | 0.11151 | 0.11327 | 0.11241 | 0.11367 | 0.11327 | 0.11327 | 0.11148 | 0.11139 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.11017 | 0.11019 | 0.11327 | 0.10928 | 0.11367 | 0.11327 | 0.11333 | 0.11017 | 0.11012 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.11281 | 0.11283 | 0.11327 | 0.1197 | 0.11367 | 0.11327 | 0.11327 | 0.11281 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.11149 | 0.11151 | 0.11327 | 0.11256 | 0.11367 | 0.11327 | 0.11327 | 0.11148 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.11017 | 0.11019 | 0.11327 | 0.10948 | 0.11367 | 0.11327 | 0.11327 | 0.11017 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.11121 | 0.11123 | 0.11327 | 0.11109 | 0.11367 | 0.11327 | 0.11327 | 0.11121 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.1099 | 0.10991 | 0.11327 | 0.10983 | 0.11367 | 0.11327 | 0.11327 | 0.1099 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.33551 | 0.33555 | 0.3398 | 0.32941 | 0.34102 | 0.3398 | 0.3398 | 0.3355 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.34027 | 0.34033 | 0.3398 | 0.33309 | 0.34102 | 0.3398 | 0.3398 | 0.34028 | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Outlet Air Temperature |  | Results Column ==> | 4 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 29.3163 | 29.3262 | 29.0892 | 29.2222 | 29.0494 | 28.994 | 29.0359 | 29.309 | 29.702 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 18.5042 | 18.5 | 18.4621 | 19 | 18.5095 | 18.5195 | 18.5081 | 18.5094 | 18.5162 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 14.9386 | 14.9302 | 14.7013 | 15.2222 | 14.9265 | 14.8437 | 14.9194 | 14.9489 | 14.76 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 29.3163 | 29.3262 | 29.0892 | 28.6667 | 29.0498 | 28.9937 | 29.0359 | 29.309 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 18.5042 | 18.5 | 18.4622 | 18.4444 | 18.5093 | 18.5187 | 18.5081 | 18.5127 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 14.9386 | 14.9302 | 14.7219 | 14.6111 | 14.9264 | 14.8418 | 14.9194 | 14.949 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 18.506 | 18.5041 | 18.4632 | 18.4444 | 18.5236 | 18.5187 | 18.5198 | 18.5089 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 18.5142 | 18.5118 | 18.4552 | 18.4444 | 18.5888 | 18.5187 | 18.5759 | 18.5234 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 18.5142 | 18.5118 | 18.4446 | 18.4444 | 18.5897 | 18.5187 | 18.5759 | 18.52 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 18.5044 | 18.5025 | 18.4632 | 18.4444 | 18.5115 | 18.5187 | 18.5096 | 18.5 | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Temperature |  | Results Column ==> | 5 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 29.9222 | 29.9328 | 29.6791 | 29.2222 | 29.6355 | 29.5758 | 29.6249 | 29.9147 | 30.3161 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 19.088 | 19.0845 | 19.052 | 19 | 19.0928 | 19.1013 | 19.0971 | 19.0931 | 19.1041 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 15.5144 | 15.5066 | 15.2912 | 15.2222 | 15.5032 | 15.4255 | 15.5084 | 15.5247 | 15.3465 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 29.9222 | 29.9328 | 29.6791 | #N/A | 29.6359 | 29.5755 | 29.6249 | 29.9147 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 19.088 | 19.0845 | 19.0521 | #N/A | 19.0925 | 19.1005 | 19.0971 | 19.0964 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 15.5144 | 15.5066 | 15.3118 | #N/A | 15.5031 | 15.4236 | 15.5084 | 15.5247 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 19.0896 | 19.0883 | 19.0531 | #N/A | 19.1052 | 19.1005 | 19.1088 | 19.0924 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 19.0968 | 19.0951 | 19.0451 | #N/A | 19.1626 | 19.1005 | 19.1649 | 19.1059 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 19.0968 | 19.0951 | 19.0345 | #N/A | 19.1634 | 19.1005 | 19.1649 | 19.1025 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 19.0882 | 19.0888 | 19.0531 | #N/A | 19.0946 | 19.1005 | 19.0986 | 19.0837 | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Humidity Ratio |  | Results Column ==> | 5 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.0016041 | 0.0016042 | 0.0016416 | 0.0016 | 0.0016122 | 0.00167 | 0.0016965 | 0.0015953 | 0.0016176 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.0043252 | 0.0042844 | 0.0043367 | 0.0043 | 0.0042844 | 0.004355 | 0.004285 | 0.0043297 | 0.0043473 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.010605 | 0.010599 | 0.010296 | 0.0108 | 0.010558 | 0.010581 | 0.010585 | 0.010612 | 0.010316 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.0016041 | 0.0016041 | 0.0016416 | 0.0016 | 0.0016122 | 0.00167 | 0.0016977 | 0.0015953 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.0043252 | 0.0042845 | 0.0043367 | 0.0043 | 0.0042844 | 0.004355 | 0.004285 | 0.0043297 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.010605 | 0.0106 | 0.010306 | 0.0104 | 0.010561 | 0.01058 | 0.010585 | 0.010612 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.0058837 | 0.00585 | 0.0059 | 0.0059 | 0.005832 | 0.005916 | 0.0058378 | 0.0058881 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.013368 | 0.013367 | 0.013227 | 0.0133 | 0.013302 | 0.013424 | 0.013413 | 0.013376 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.013368 | 0.013367 | 0.013257 | 0.0133 | 0.01341 | 0.013424 | 0.013413 | 0.013373 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.0044909 | 0.0044571 | 0.00451 | 0.0045 | 0.004481 | 0.004508 | 0.0044868 | 0.0044909 | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Specific Volume |  | Results Column ==> | 5 |  | Results Row Offset==> | 2
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 860.7762 | 860.6945 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 856.5396 | 861.9203 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 833.6275 | 833.4546 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 829.5769 | 833.7092 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 831.6898 | 831.5517 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 827.6673 | 830.8336 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 860.7762 | 860.6945 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 856.5396 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 833.6275 | 833.4546 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 829.5862 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 831.6898 | 831.5517 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 827.6674 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 835.7063 | 835.549 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 831.6391 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 845.6895 | 845.5719 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 841.5963 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 845.6895 | 845.5719 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 841.5827 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 833.8485 | 833.6965 | 833.33 | #N/A | 830.3519 | #N/A | 833 | 829.7636 | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Enthalpy |  | Results Column ==> | 5 |  | Results Row Offset==> | 3
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 34.2029 | #N/A | 34.02 | #N/A | 33.8997 | #N/A | 34.1363 | 34.1729 | 34.6348 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 30.1736 | #N/A | 30.14 | #N/A | 30.0522 | #N/A | 30.0761 | 30.1899 | 30.2457 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 42.4358 | #N/A | 41.4 | #N/A | 42.2878 | #N/A | 42.3718 | 42.4646 | 41.5345 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 34.2055 | #N/A | 34.02 | #N/A | 33.9001 | #N/A | 34.1393 | 34.1729 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 30.1752 | #N/A | 30.14 | #N/A | 30.0519 | #N/A | 30.0761 | 30.1932 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 42.4371 | #N/A | 41.44 | #N/A | 42.2941 | #N/A | 42.3718 | 42.4647 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 34.1298 | #N/A | 34.1 | #N/A | 33.9902 | #N/A | 34.0251 | 34.1421 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 53.121 | #N/A | 52.67 | #N/A | 52.9973 | #N/A | 53.29 | 53.1486 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 53.121 | #N/A | 52.74 | #N/A | 53.2723 | #N/A | 53.29 | 53.1378 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 30.5955 | #N/A | 30.58 | #N/A | 30.5528 | #N/A | 30.5893 | 30.5893 | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Mass Flow Rate |  | Results Column ==> | 5 |  | Results Row Offset==> | 4
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.32963 | 0.32966 | 0.3398 | 0.35862 | 0.34102 | 0.3398 | 0.3398 | 0.32964 | 0.32961 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.34036 | 0.34043 | 0.3398 | 0.33724 | 0.34102 | 0.3398 | 0.3398 | 0.34035 | 0.34034 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.34115 | 0.34121 | 0.3398 | 0.32785 | 0.34102 | 0.3398 | 0.3398 | 0.34114 | 0.34145 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.32963 | 0.32966 | 0.3398 | 0.35909 | 0.34102 | 0.3398 | 0.3398 | 0.32964 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.34036 | 0.34043 | 0.3398 | 0.33768 | 0.34102 | 0.3398 | 0.3398 | 0.34035 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.34115 | 0.34121 | 0.3398 | 0.32843 | 0.34102 | 0.3398 | 0.3398 | 0.34114 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.33952 | 0.33958 | 0.3398 | 0.33327 | 0.34102 | 0.3398 | 0.3398 | 0.33951 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.33551 | 0.33555 | 0.3398 | 0.32948 | 0.34102 | 0.3398 | 0.3398 | 0.33549 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.33551 | 0.33555 | 0.3398 | 0.32941 | 0.34102 | 0.3398 | 0.3398 | 0.3355 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.34027 | 0.34033 | 0.3398 | 0.33309 | 0.34102 | 0.3398 | 0.3398 | 0.34028 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone Air Temperature |  | Results Column ==> | 6 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 21.1111 | 21.1111 | 21.0991 | 21.1111 | 21.1183 | 21.111 | 21.111 | 21.1138 | 21.111 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 23.3333 | 23.3333 | 23.3479 | 23.3333 | 23.3293 | 23.3321 | 23.333 | 23.3325 | 23.333 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 23.8889 | 23.8889 | 23.8764 | 23.8889 | 23.8823 | 23.8901 | 23.889 | 23.8905 | 23.889 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 21.1111 | 21.1111 | 21.099 | 21.1111 | 21.1187 | 21.1107 | 21.111 | 21.1138 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 23.3333 | 23.3333 | 23.3481 | 23.3333 | 23.3288 | 23.3313 | 23.333 | 23.3358 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 23.8889 | 23.8889 | 23.897 | 23.8889 | 23.8822 | 23.8882 | 23.889 | 23.8905 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 23.3333 | 23.3333 | 23.3479 | 23.3333 | 23.3296 | 23.3313 | 23.333 | 23.3302 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 23.3333 | 23.3333 | 23.3378 | 23.3333 | 23.33 | 23.3313 | 23.333 | 23.3365 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 23.3333 | 23.3333 | 23.3272 | 23.3333 | 23.33 | 23.3313 | 23.333 | 23.3331 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 23.3333 | 23.3333 | 23.3479 | 23.3333 | 23.3294 | 23.3313 | 23.333 | 23.3227 | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Fan Temperature Rise (°C)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.60585 | 0.60658 | 0.5899 | 0 | 0.58614 | 0.5818 | 0.589 | 0.60572 | 0.61414 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.58381 | 0.58449 | 0.5899 | 0 | 0.58327 | 0.5818 | 0.589 | 0.58371 | 0.58791 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.57583 | 0.57646 | 0.5899 | 0 | 0.57663 | 0.5818 | 0.589 | 0.57574 | 0.58647 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.60585 | 0.60658 | 0.5899 | #N/A | 0.58614 | 0.5818 | 0.589 | 0.60572 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.58381 | 0.58449 | 0.5899 | #N/A | 0.58327 | 0.5818 | 0.589 | 0.58372 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.57583 | 0.57646 | 0.5899 | #N/A | 0.57663 | 0.5818 | 0.589 | 0.57574 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.5836 | 0.58428 | 0.5899 | #N/A | 0.58162 | 0.5818 | 0.589 | 0.5835 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.58261 | 0.58329 | 0.5899 | #N/A | 0.57377 | 0.5818 | 0.589 | 0.5825 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.58261 | 0.58329 | 0.5899 | #N/A | 0.57366 | 0.5818 | 0.589 | 0.5825 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.58379 | 0.58632 | 0.5899 | #N/A | 0.58306 | 0.5818 | 0.589 | 0.58367 | #N/A | #N/A | #N/A | #N/A | #N/A
Return Fan Temperature Rise (°C)
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.27209 | 0.295 | 0.29495 | 0.27778 | 0.28973 | 0.2909 | 0.295 | 0.27201 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.31262 | 0.29704 | 0.29495 | 0.27778 | 0.29127 | 0.2909 | 0.295 | 0.31247 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.32615 | 0.29715 | 0.29495 | 0.27778 | 0.28796 | 0.2909 | 0.295 | 0.326 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.3125 | 0.29693 | 0.29495 | 0.33333 | 0.29045 | 0.2909 | 0.295 | 0.31234 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.31193 | 0.29641 | 0.29495 | 0.27778 | 0.28654 | 0.2909 | 0.295 | 0.31178 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.31193 | 0.29641 | 0.29495 | 0.33333 | 0.28648 | 0.2909 | 0.295 | 0.31179 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.3126 | 0.29703 | 0.29495 | 0.33333 | 0.29117 | 0.2909 | 0.295 | 0.31245 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone Humidity Ratio Rise (gw/gda) |  |  |  |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.00069993 | 0.00069989 | 0.00069081 | 0.0006 | 0.00067658 | 0.0007 | 0.00067658 | 0.00069532 | 0.00071869 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.00067676 | 0.00067661 | 0.00069436 | 0.0007 | 0.00067549 | 0.000704 | 0.00067552 | 0.00067892 | 0.000688 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.00067491 | 0.00067482 | 0.00068973 | 0.0007 | 0.00067521 | 0.000704 | 0.00067525 | 0.00067917 | 0.0006874 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.00069993 | 0.00069996 | 0.00069081 | 0.0006 | 0.00067658 | 0.000704 | 0.00067658 | 0.00069532 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.00067676 | 0.00067654 | 0.00069436 | 0.0007 | 0.00067549 | 0.000704 | 0.00067552 | 0.00067893 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.00067491 | 0.00067481 | 0.00068973 | 0.0007 | 0.00067521 | 0.000704 | 0.00067525 | 0.00067917 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.00067844 | 0.00067834 | 0.00069308 | 0.0007 | 0.00067549 | 0.000704 | 0.00067552 | 0.00068061 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.00068655 | 0.00068648 | 0.00069436 | 0.0007 | 0.00067549 | 0.000704 | 0.00067552 | 0.00068876 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.00068655 | 0.00068648 | 0.00069436 | 0.0008 | 0.00067549 | 0.000704 | 0.00067552 | 0.00068875 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.00067694 | 0.00067683 | 0.00069436 | 0.0007 | 0.00067549 | 0.000704 | 0.00067552 | 0.00067908 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone Humidity Ratio (gw/gda) |  |  |  |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.002304 | 0.0023041 | 0.0023324 | 0.0022 | 0.0022887 | 0.00237 | 0.0023731 | 0.0022906 | 0.0023363 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.005002 | 0.0049611 | 0.0050311 | 0.005 | 0.0049599 | 0.005059 | 0.0049605 | 0.0050086 | 0.0050353 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.01128 | 0.011274 | 0.010986 | 0.0115 | 0.011233 | 0.011285 | 0.011261 | 0.011291 | 0.011004 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.002304 | 0.0023041 | 0.0023324 | 0.0022 | 0.0022887 | 0.002374 | 0.0023743 | 0.0022906 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.005002 | 0.0049611 | 0.0050311 | 0.005 | 0.0049599 | 0.005059 | 0.0049605 | 0.0050086 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.01128 | 0.011274 | 0.010995 | 0.0111 | 0.011236 | 0.011284 | 0.011261 | 0.011291 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.0065621 | 0.0065284 | 0.0065931 | 0.0066 | 0.0065075 | 0.00662 | 0.0065133 | 0.0065687 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.014054 | 0.014053 | 0.013921 | 0.014 | 0.013978 | 0.014128 | 0.014089 | 0.014065 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.014054 | 0.014053 | 0.013951 | 0.0141 | 0.014086 | 0.014128 | 0.014089 | 0.014062 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.0051678 | 0.005134 | 0.0052044 | 0.0052 | 0.0051565 | 0.005212 | 0.0051623 | 0.00517 | #N/A | #N/A | #N/A | #N/A | #N/A
Zone Latent Gain (gw/s) |  |  |  |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.23072 | 0.23072 | 0.23474 | 0.21517 | 0.23073 | 0.23786 | 0.22991 | 0.22921 | 0.23689 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.23034 | 0.23034 | 0.23595 | 0.23607 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | 0.23415 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.23025 | 0.23026 | 0.23437 | 0.2295 | 0.23026 | 0.23922 | 0.22945 | 0.23169 | 0.23471 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.23072 | 0.23075 | 0.23474 | 0.21546 | 0.23073 | 0.23922 | 0.22991 | 0.22921 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.23034 | 0.23032 | 0.23595 | 0.23638 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.23025 | 0.23025 | 0.23437 | 0.2299 | 0.23026 | 0.23922 | 0.22945 | 0.23169 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.23034 | 0.23035 | 0.23551 | 0.23329 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.23034 | 0.23035 | 0.23595 | 0.23064 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 0.23034 | 0.23035 | 0.23595 | 0.26353 | 0.23036 | 0.23922 | 0.22954 | 0.23107 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 0.23034 | 0.23035 | 0.23595 | 0.23316 | 0.23036 | 0.23922 | 0.22954 | 0.23108 | #N/A | #N/A | #N/A | #N/A | #N/A

## Delta Results
Output spreadsheet for Airside HVAC BESTEST
Aggregator Sheet - DELTA RESULTS for Delta Plots
Total Heating and Cooling Loads
Tab Name==>
Cases | QAS | DEEAP | DeST | DOE22 | EPlus | IES-VE | LCEM | TRNSYS | YourData | Blank | Blank | Blank | Blank
| QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE201-AE101 Heating -29.0/-29.0 | -0.059605 | -0.064549 | -0.067382 | -0.058321 | -0.066421 | -0.067 | -0.070108 | -0.059584 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203-AE103 Dry Coil Cooling 15.5/-3.0 | 0.072652 | 0.068956 | 0.067631 | 0.063303 | 0.067154 | 0.068 | 0.067746 | 0.072468 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204-AE104 Wet Coil Cooling Total Coil Load 26.9/22.1 | 0.077372 | 0.07042 | 0.06085 | 0.17848 | 0.066443 | 0.068 | 0.067691 | 0.077318 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204-AE104 Wet Coil Cooling Sensible Coil Load 26.9/22.1 | 0.077372 | 0.07042 | 0.06503 | 0.069165 | 0.067164 | 0.067 | 0.066631 | 0.077323 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204-AE104 Wet Coil Cooling Latent Coil Load 26.9/22.1 | 0 | -5.7732e-15 | -0.0041804 | 0.10932 | -0.00072059 | 0.001 | 0.0010596 | -5.7975e-06 | #N/A | #N/A | #N/A | #N/A | #N/A
Economizer
Tab Name==>
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
Total Cooling | 0.2914 | 0.29211 | 0.28703 | 0.2793 | 0.29465 | 0.295 | 0.29113 | 0.29622 | #N/A | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | 0.2914 | 0.29211 | 0.28703 | 0.2793 | 0.29465 | 0.295 | 0.29161 | 0.29622 | #N/A | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | -0.00047276 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Total Cooling | 0.68493 | 0.67125 | 0.82473 | 0.67348 | 0.67988 | 0.681 | 0.69228 | 0.68443 | #N/A | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | -0.14458 | -0.14373 | -0.13841 | -0.12602 | -0.14185 | -0.143 | -0.14226 | -0.143 | #N/A | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 0.82951 | 0.81497 | 0.96314 | 0.7995 | 0.82172 | 0.825 | 0.83454 | 0.82743 | #N/A | #N/A | #N/A | #N/A | #N/A
Temperature
DB | AE101 | AE102 | AE103 | AE104 | AE105 | AE106
Original DB | -20 | 30 | 60 | 80 | 77 | 74
New DB | -20.2 | 30.02 | 59.9 | 80.42 | 76.82 | 73.4
Original WB | -20 | 20 | 45 | 75 | 55 | 70
New WB | -20.2 | 19.756 | 44.972 | 74.191 | 55.452 | 70.744
Outdoor Air Fraction
Cases | QAS/PSU-TAMU-NREL | DEEAP/AAON | DeST/TsinghuaU-LBNL | DOE-2.2/NREL | EnergyPlus/GARD | IES-VE/IES | LCEM/MLIT-TTE | TRNSYS/TESS | OpenSimula/US | Blank | Blank | Blank | Blank
AE101 FC Heat -29.0/-29.0 | 0.34224 | 0.34226 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33353 | 0.34223 | 0.34597 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | 0.3273 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.32294 | 0.32294 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33353 | 0.32295 | 0.32252 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.34224 | 0.34226 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.34223 | #N/A | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | #N/A | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.32294 | 0.32294 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32295 | #N/A | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | #N/A | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.32756 | 0.32756 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32757 | #N/A | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Original Case Conditions |  | New Case Conditions |  | June 13th 2012 case conditions
| Case | DB (°F) | WB (°F) | DB (°F) | WB (°F) | DB (°C) | WB (°C)
| AE101 | -20 | -20 | -20.2 | -20.2 | -29 | -29
| AE102 | 30 | 20 | 30.02 | 19.756
| AE103 | 60 | 45 | 59.9 | 44.972 | 15.5 | 7.2
| AE104 | 80 | 75 | 80.42 | 74.191 | 26.9 | 23.4
| AE105 | 77 | 55 | 76.82 | 55.452 | 24.9 | 13.03
| AE106 | 74 | 70 | 73.4 | 70.744 | 23 | 21.5

## QAS
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Quasi-Analytical Solution V2 | [5 empty] | National Renewable Energy Laboratory
1. Use specified units. |  |  |  | Program Version Release Date: |  |  |  | 2014-10-10 |  | Modeler Organization for Tables and Charts (short): |  |  |  | PSU-TAMU-NREL
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | QAS
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2014-11-12 |  | Model / Organization Indentifier for Charts (short): |  |  |  | QAS/PSU-TAMU-NREL
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | Quasi-analytic Solution
| Version: | V2
| Date: | 2014-11-12
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZCsensible) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9307 | 0 | 0.58614 | 8.4195 | 0 | 0 | 0 | 6.3854 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.0034 | 29.3163 | 29.3163 | 29.9222 | 21.1111 | 21.1111
| AE103 | 0 | 1.4654 | 0.58614 | 0 | 0.78348 | 0 | 0.78348 | 32.8432 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016041 | 0.002304 | 0.002304
| AE104 | 0 | 2.9307 | 0.58614 | 0 | 3.4965 | 2.0543 | 5.5508 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9314 | 787.1625 | 859.0555 | 859.0555 | 860.7762 | 836.6895 | 836.6895
[16 empty] | Enthalpy (J/gda) | -28.5404 | 8.0513 | 33.5916 | 33.5916 | 34.2029 | 27.0907 | 27.0907
[16 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32963 | 0.32963 | 0.32963 | 0.32963 | #N/A | 0.21681
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7741 | 20.7741 | 18.5042 | 19.088 | 23.3333 | 23.3333
[16 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043252 | 0.0043252 | 0.0043252 | 0.0043252 | 0.005002 | 0.005002
[16 empty] | Specific volume (L/kgda) | 821.5658 | 838.437 | 838.437 | 831.9622 | 833.6275 | 846.6514 | 846.6514
[16 empty] | Enthalpy (J/gda) | 23.0203 | 31.8833 | 31.8833 | 29.5815 | 30.1736 | 36.2004 | 36.2004
[16 empty] | Mass flow rate (kgda/s) | 0.11149 | 0.34036 | 0.34036 | 0.34036 | 0.34036 | #N/A | 0.22888
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8678 | 24.8678 | 14.9386 | 15.5144 | 23.8889 | 23.8889
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013054 | 0.013054 | 0.010605 | 0.010605 | 0.01128 | 0.01128
[16 empty] | Specific volume (L/kgda) | 872.9245 | 861.9632 | 861.9632 | 830.0307 | 831.6898 | 856.7312 | 856.7312
[16 empty] | Enthalpy (J/gda) | 69.8513 | 58.2685 | 58.2685 | 41.8451 | 42.4358 | 52.7436 | 52.7436
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | #N/A | 0.23098
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZCsensible) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9307 | 0 | 0.58614 | 8.3599 | 0 | 0 | 0 | 6.3854 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.1826 | 29.3163 | 29.3163 | 29.9222 | 21.1111 | 21.1111 | 21.3832
| AE203 | 0 | 1.4654 | 0.58614 | 0 | 0.85614 | 0 | 0.85614 | 32.8432 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016041 | 0.002304 | 0.002304 | 0.002304
| AE204 | 0 | 2.9307 | 0.58614 | 0 | 3.5739 | 2.0543 | 5.6282 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9314 | 787.6715 | 859.0555 | 859.0555 | 860.7762 | 836.6895 | 836.6895 | 837.4631
| AE205 | 0 | 1.4654 | 0.58614 | 0 | 1.9163 | 0 | 1.9163 | 44.5612 | [6 empty] | Enthalpy (J/gda) | -28.5429 | 8.2324 | 33.5942 | 33.5942 | 34.2055 | 27.0925 | 27.0925 | 27.3675
| AE206 | 0 | 1.4654 | 0.58614 | 0 | 1.7064 | 0.97038 | 2.6768 | 100 | [6 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32963 | 0.32963 | 0.32963 | 0.32963 | #N/A | 0.21681 | 0.21681
| AE226 | 0 | 1.4654 | 0.58614 | 0 | 1.5618 | 1.7999 | 3.3617 | 100 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9845 | 20.9845 | 18.5042 | 19.088 | 23.3333 | 23.3333 | 23.6459
| AE245 | 0 | 1.4654 | 0.58614 | 0 | 2.2077 | 0 | 2.2077 | 34.0915 | [6 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043252 | 0.0043252 | 0.0043252 | 0.0043252 | 0.005002 | 0.005002 | 0.005002
[16 empty] | Specific volume (L/kgda) | 821.5658 | 839.0374 | 839.0374 | 831.9622 | 833.6275 | 846.6514 | 846.6514 | 847.5441
[16 empty] | Enthalpy (J/gda) | 23.0217 | 32.0985 | 32.0985 | 29.5832 | 30.1752 | 36.2025 | 36.2025 | 36.5199
[16 empty] | Mass flow rate (kgda/s) | 0.11149 | 0.34036 | 0.34036 | 0.34036 | 0.34036 | #N/A | 0.22888 | 0.22888
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.088 | 25.088 | 14.9386 | 15.5144 | 23.8889 | 23.8889 | 24.215
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013054 | 0.013054 | 0.010605 | 0.010605 | 0.01128 | 0.01128 | 0.01128
[16 empty] | Specific volume (L/kgda) | 872.9245 | 862.5998 | 862.5998 | 830.0307 | 831.6898 | 856.7312 | 856.7312 | 857.6719
[16 empty] | Enthalpy (J/gda) | 69.8537 | 58.4974 | 58.4974 | 41.8464 | 42.4371 | 52.7457 | 52.7457 | 53.0807
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34115 | 0.34115 | 0.34115 | 0.34115 | #N/A | 0.23098 | 0.23098
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0556 | 24.0556 | 18.506 | 19.0896 | 23.3333 | 23.3333 | 23.6458
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0058837 | 0.0058837 | 0.0058837 | 0.0058837 | 0.0065621 | 0.0065621 | 0.0065621
[16 empty] | Specific volume (L/kgda) | 850.4314 | 849.9075 | 849.9075 | 834.0374 | 835.7063 | 848.7583 | 848.7583 | 849.6529
[16 empty] | Enthalpy (J/gda) | 36.4912 | 39.1804 | 39.1804 | 33.5362 | 34.1298 | 40.172 | 40.172 | 40.4903
[16 empty] | Mass flow rate (kgda/s) | 0.11121 | 0.33952 | 0.33952 | 0.33952 | 0.33952 | #N/A | 0.22831 | 0.22831
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4335 | 23.4335 | 18.5142 | 19.0968 | 23.3333 | 23.3333 | 23.6453
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014546 | 0.014546 | 0.013368 | 0.013368 | 0.014054 | 0.014054 | 0.014054
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.8306 | 859.8306 | 844.0036 | 845.6895 | 858.8761 | 858.8761 | 859.7797
[16 empty] | Enthalpy (J/gda) | 62.7099 | 60.5901 | 60.5901 | 52.5203 | 53.121 | 59.2355 | 59.2355 | 59.5574
[16 empty] | Mass flow rate (kgda/s) | 0.1099 | 0.33551 | 0.33551 | 0.33551 | 0.33551 | #N/A | 0.22561 | 0.22561
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5142 | 19.0968 | 23.3333 | 23.3333 | 23.6453
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.013368 | 0.013368 | 0.014054 | 0.014054 | 0.014054
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.9354 | 859.9354 | 844.0036 | 845.6895 | 858.8761 | 858.8761 | 859.7797
[16 empty] | Enthalpy (J/gda) | 62.7099 | 62.7099 | 62.7099 | 52.5203 | 53.121 | 59.2355 | 59.2355 | 59.5574
[16 empty] | Mass flow rate (kgda/s) | 0.33551 | 0.33551 | 0.33551 | 0.33551 | 0.33551 | #N/A | 0.22561 | 0.22561
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5044 | 19.0882 | 23.3333 | 23.3333 | 23.6459
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0051678 | 0.0051678 | 0.0051678
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4314 | 850.4314 | 832.1827 | 833.8485 | 846.8753 | 846.8753 | 847.7683
[16 empty] | Enthalpy (J/gda) | 36.4912 | 36.4912 | 36.4912 | 30.0033 | 30.5955 | 36.6243 | 36.6243 | 36.9419
[16 empty] | Mass flow rate (kgda/s) | 0.34027 | 0.34027 | 0.34027 | 0.34027 | 0.34027 | #N/A | 0.22882 | 0.22882
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Load | Load | Load | Load | Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 2.947 | 0 | 0 | 0 | 24.7331 | 7.7129 | 8.3889 | AE301 | Dry bulb temperature (°C) | -29 | 3.4316 | 7.2222 | 7.2222 | 7.7838 | 29.2787 | 27.8228 | 21.1111 | 22.2222 | 21.6708 | 22.019
| AE303 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 6.7354 | 0 | 6.7354 | 48.1495 | 2.2584 | 2.4572 |  | Humidity ratio (g/gda) | 0.00025893 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0015483 | 0.0021971 | 0.0023817 | 0.0022901 | 0.0022901
| AE304 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 10.3202 | 6.2583 | 16.5785 | 100 | 0.99332 | 1.519 |  | Specific volume (L/kgda) | 691.9314 | 785.4683 | 796.2333 | 796.2333 | 797.8282 | 858.8717 | 854.7372 | 836.5461 | 839.9533 | 838.262 | 839.252
| AE305 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.3829 | 0 | 9.3829 | 65.719 | 2.2598 | 2.4589 |  | Enthalpy (J/gda) | -28.5429 | 7.3347 | 11.1593 | 11.1593 | 11.726 | 33.4136 | 31.9447 | 26.8208 | 28.4127 | 27.6225 | 27.9743
| AE306 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.9211 | 5.4432 | 14.3643 | 100 | 2.2625 | 2.4624 |  | Mass flow rate (kgda/s) | 0.28139 | 0.77054 | 0.77054 | 0.77054 | 0.77054 | 0.35564 | 0.41491 | #N/A | #N/A | 0.48915 | 0.48915
| AE326 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.4609 | 12.3018 | 20.7626 | 100 | 2.2625 | 2.4624 | AE303 | Dry bulb temperature (°C) | 15.5 | 21.0184 | 21.0184 | 12.2066 | 12.7778 | 19.1796 | 18.7479 | 23.3333 | 24.4444 | 23.8924 | 24.232
| AE345 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.7029 | 0 | 9.7029 | 51.0891 | 2.2587 | 2.4575 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0042307 | 0.0048927 | 0.0050812 | 0.0049876 | 0.0049876
[16 empty] | Specific volume (L/kgda) | 821.5658 | 839.0074 | 839.0074 | 813.8748 | 815.504 | 833.7629 | 832.5316 | 846.5039 | 849.9317 | 848.2283 | 849.198
[16 empty] | Enthalpy (J/gda) | 23.0217 | 31.8928 | 31.8928 | 22.9579 | 23.5371 | 30.0283 | 29.5906 | 35.9245 | 37.5324 | 36.7334 | 37.0782
[16 empty] | Mass flow rate (kgda/s) | 0.27809 | 0.75384 | 0.75384 | 0.75384 | 0.75384 | 0.34793 | 0.40591 | #N/A | #N/A | 0.47575 | 0.47575
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5732 | 25.5732 | 12.2072 | 12.7778 | 15.5904 | 16.4644 | 23.8889 | 25 | 24.4481 | 24.7899
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.01225 | 0.01225 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0095185 | 0.0097082 | 0.0096139 | 0.0096139
[16 empty] | Specific volume (L/kgda) | 872.9245 | 862.9099 | 862.9099 | 819.8829 | 821.5223 | 829.6035 | 832.1147 | 854.3485 | 857.802 | 856.0862 | 857.0696
[16 empty] | Enthalpy (J/gda) | 69.8537 | 56.9493 | 56.9493 | 34.6208 | 35.2043 | 38.0804 | 38.9741 | 48.2629 | 49.8839 | 49.0785 | 49.4286
[16 empty] | Mass flow rate (kgda/s) | 0.27554 | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.34538 | 0.40294 | #N/A | #N/A | 0.47278 | 0.47278
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4777 | 24.4777 | 12.2068 | 12.7778 | 19.1811 | 18.75 | 23.3333 | 24.4444 | 23.8924 | 24.2318
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0057889 | 0.0064526 | 0.0066415 | 0.0065476 | 0.0065476
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.9862 | 850.9862 | 815.9007 | 817.5333 | 835.842 | 834.6093 | 848.6104 | 852.0467 | 850.3391 | 851.3109
[16 empty] | Enthalpy (J/gda) | 36.4912 | 39.3684 | 39.3684 | 26.8906 | 27.4712 | 33.9825 | 33.5441 | 39.8934 | 41.5057 | 40.7045 | 41.0501
[16 empty] | Mass flow rate (kgda/s) | 0.2774 | 0.75197 | 0.75197 | 0.75197 | 0.75197 | 0.34706 | 0.40491 | #N/A | #N/A | 0.47457 | 0.47457
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7742 | 23.7742 | 12.2072 | 12.7778 | 19.1841 | 18.7541 | 23.3333 | 24.4444 | 23.8924 | 24.2316
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.011806 | 0.011806 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0095187 | 0.0097086 | 0.0096142 | 0.0096142
[16 empty] | Specific volume (L/kgda) | 859.9354 | 857.1123 | 857.1123 | 819.8829 | 821.5223 | 839.9288 | 838.6933 | 852.751 | 856.2041 | 854.4881 | 855.4639
[16 empty] | Enthalpy (J/gda) | 62.7099 | 53.9677 | 53.9677 | 34.6208 | 35.2043 | 41.7551 | 41.3154 | 47.6948 | 49.3158 | 48.5103 | 48.8576
[16 empty] | Mass flow rate (kgda/s) | 0.27605 | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.34538 | 0.40294 | #N/A | #N/A | 0.47227 | 0.47227
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2072 | 12.7778 | 19.1841 | 18.7541 | 23.3333 | 24.4444 | 23.8924 | 24.2316
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0088518 | 0.0095187 | 0.0097086 | 0.0096142 | 0.0096142
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.9354 | 859.9354 | 819.8829 | 821.5223 | 839.9288 | 838.6933 | 852.751 | 856.2041 | 854.4881 | 855.4639
[16 empty] | Enthalpy (J/gda) | 62.7099 | 62.7099 | 62.7099 | 34.6208 | 35.2043 | 41.7551 | 41.3154 | 47.6948 | 49.3158 | 48.5103 | 48.8576
[16 empty] | Mass flow rate (kgda/s) | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.74832 | 0.34538 | 0.40294 | #N/A | #N/A | 0.47227 | 0.47227
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.2066 | 12.7778 | 19.1799 | 18.7483 | 23.3333 | 24.4444 | 23.8924 | 24.2319
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0051532 | 0.0053417 | 0.005248 | 0.005248
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4314 | 850.4314 | 814.213 | 815.8428 | 834.11 | 832.8785 | 846.8556 | 850.2849 | 848.5808 | 849.5508
[16 empty] | Enthalpy (J/gda) | 36.4912 | 36.4912 | 36.4912 | 23.6145 | 24.194 | 30.6885 | 30.2507 | 36.5871 | 38.1958 | 37.3964 | 37.7413
[16 empty] | Mass flow rate (kgda/s) | 0.75353 | 0.75353 | 0.75353 | 0.75353 | 0.75353 | 0.34778 | 0.40575 | #N/A | #N/A | 0.47555 | 0.47555
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 |  | Zone 1 | Zone 2 |  | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible |  | Latent | Sensible |  | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Load |  | Load | Load |  | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZC1sensible) |  | (QZ1latent) | (QZC2sensible) |  | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) |  | (kWh/h) | (kWh/h) |  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9307 | 0 | 0.58614 | 2.3446 | 0 | 0.87921 | 10.2597 | 0 | 0 | 0 | 4.1447 | 4.4994 | 4.8772 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.2222 | 7.2222 | 7.2968 | 46.92 | 36.0391 | 21.1111 | 22.2222 | #N/A | #N/A
| AE403 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 1.458 | 0 | 1.458 | 36.3949 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00025893 | 0.002304 | 0.0023101 | #N/A | #N/A
| AE404 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 7.399 | 5.9242 | 13.3232 | 100 | 0 | 0 |  | Specific volume (L/kgda) | 691.9314 | 691.9314 | 794.5867 | 794.5867 | 794.7981 | 907.0919 | 876.2548 | 836.6895 | 839.8569 | #N/A | #N/A
| AE405 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1023 | 0 | 4.1023 | 53.4629 | 0 | 0 |  | Enthalpy (J/gda) | -28.5429 | -28.5429 | 7.9172 | 7.9172 | 7.9923 | 47.8758 | 36.9234 | 27.0925 | 28.2306 | #N/A | #N/A
| AE406 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6354 | 4.5879 | 8.2233 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28139 | 0.28139 | 0.28139 | 0.28139 | 0.28139 | 0.11281 | 0.16858 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.5938 | 5.2366 | 8.8305 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9553 | 16.9553 | 12.6643 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9495 | 23.9545
| AE445 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1575 | 0 | 4.1575 | 49.575 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0032906 | 0.0049701 | 0.0050294 | 0.005003 | 0.005003
[16 empty] | Specific volume (L/kgda) | 821.5658 | 826.1765 | 826.1765 | 813.9564 | 814.2796 | 814.2796 | 814.2796 | 846.6083 | 849.8616 | 848.4124 | 848.4267
[16 empty] | Enthalpy (J/gda) | 23.0217 | 25.392 | 25.392 | 21.0486 | 21.1635 | 21.1635 | 21.1635 | 36.1213 | 37.4006 | 36.8307 | 36.8358
[16 empty] | Mass flow rate (kgda/s) | 0.27809 | 0.33569 | 0.33569 | 0.33569 | 0.33569 | 0.13715 | 0.19854 | #N/A | #N/A | 0.057601 | 0.057601
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.7259 | 25.7259 | 12.4805 | 12.7778 | 12.7778 | 12.7778 | 23.8889 | 25 | 24.3792 | 24.4858
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013486 | 0.013486 | 0.0090147 | 0.0090147 | 0.0090147 | 0.0090147 | 0.0099076 | 0.010241 | 0.010055 | 0.010055
[16 empty] | Specific volume (L/kgda) | 872.9245 | 865.0327 | 865.0327 | 820.8802 | 821.7345 | 821.7345 | 821.7345 | 854.875 | 858.5261 | 856.4857 | 856.7924
[16 empty] | Enthalpy (J/gda) | 69.8537 | 60.2554 | 60.2554 | 35.3116 | 35.6156 | 35.6156 | 35.6156 | 49.2534 | 51.2422 | 50.1307 | 50.2399
[16 empty] | Mass flow rate (kgda/s) | 0.27533 | 0.53919 | 0.53919 | 0.53919 | 0.53919 | 0.25787 | 0.28132 | #N/A | #N/A | 0.26386 | 0.26386
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7375 | 24.7375 | 12.6644 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9495 | 23.9544
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0048458 | 0.0065301 | 0.0065896 | 0.0065631 | 0.0065631
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4494 | 850.4494 | 815.9814 | 816.3051 | 816.3051 | 816.3051 | 848.715 | 851.9764 | 850.5234 | 850.5376
[16 empty] | Enthalpy (J/gda) | 36.4912 | 37.2305 | 37.2305 | 24.975 | 25.0901 | 25.0901 | 25.0901 | 40.0906 | 41.3736 | 40.802 | 40.807
[16 empty] | Mass flow rate (kgda/s) | 0.2774 | 0.33473 | 0.33473 | 0.33473 | 0.33473 | 0.13676 | 0.19797 | #N/A | #N/A | 0.057335 | 0.057335
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1615 | 23.1615 | 12.6647 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9492 | 23.9541
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014755 | 0.014755 | 0.009126 | 0.009126 | 0.009126 | 0.009126 | 0.010823 | 0.010883 | 0.010857 | 0.010857
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.3233 | 859.3233 | 821.5545 | 821.8794 | 821.8794 | 821.8794 | 854.5129 | 857.7967 | 856.333 | 856.3471
[16 empty] | Enthalpy (J/gda) | 62.7099 | 60.8393 | 60.8393 | 35.7809 | 35.8965 | 35.8965 | 35.8965 | 51.0146 | 52.3077 | 51.7313 | 51.7363
[16 empty] | Mass flow rate (kgda/s) | 0.27552 | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.13569 | 0.19643 | #N/A | #N/A | 0.056614 | 0.056614
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6647 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9492 | 23.9541
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.009126 | 0.009126 | 0.009126 | 0.009126 | 0.010823 | 0.010883 | 0.010857 | 0.010857
[16 empty] | Specific volume (L/kgda) | 859.9354 | 859.9354 | 859.9354 | 821.5545 | 821.8794 | 821.8794 | 821.8794 | 854.5129 | 857.7967 | 856.333 | 856.3471
[16 empty] | Enthalpy (J/gda) | 62.7099 | 62.7099 | 62.7099 | 35.7809 | 35.8965 | 35.8965 | 35.8965 | 51.0146 | 52.3077 | 51.7313 | 51.7363
[16 empty] | Mass flow rate (kgda/s) | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.33213 | 0.13569 | 0.19643 | #N/A | #N/A | 0.056614 | 0.056614
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6644 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9495 | 23.9544
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0061741 | 0.0062336 | 0.0062071 | 0.0062071
[16 empty] | Specific volume (L/kgda) | 850.4314 | 850.4314 | 850.4314 | 815.5192 | 815.8428 | 815.8428 | 815.8428 | 848.2342 | 851.4937 | 850.0416 | 850.0558
[16 empty] | Enthalpy (J/gda) | 36.4912 | 36.4912 | 36.4912 | 24.0789 | 24.194 | 24.194 | 24.194 | 39.1847 | 40.4668 | 39.8956 | 39.9007
[16 empty] | Mass flow rate (kgda/s) | 0.33495 | 0.33495 | 0.33495 | 0.33495 | 0.33495 | 0.13685 | 0.1981 | #N/A | #N/A | 0.057395 | 0.057395
* n/a = not applicable

## DEEAP
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | AAON Detailed Energy and Economic Analysis Program 1.1.2 | [5 empty] | AAON Inc.
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | AAON
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | DEEAP
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2012-12-10 |  | Model / Organization Indentifier for Charts (short): |  |  |  | DEEAP/AAON
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | AAON Detailed Energy and Economics Analysis Program
| Version: | 1.1.2
| Date: | 2012-12-10
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9309 |  | 0.58608 | 8.4133 | 0 | 0 | 0 | 6.3813 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.0029 | 29.3262 | 29.3262 | 29.9328 | 21.1111
| AE103 |  | 1.4649 | 0.586 | 0 | 0.78407 | 0 | 0.78407 | 32.5417 | [6 empty] | Humidity ratio (g/gda) | 0.00025894 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016042 | 0.0023041
| AE104 |  | 2.9303 | 0.58608 | 0 | 3.4882 | 2.0648 | 5.553 | 99.9992 | [6 empty] | Specific volume (L/kgda) | 691.8414 | 787.0586 | 858.9719 | 858.9719 | 860.6945 | 836.5805
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11283 | 0.32966 | 0.32966 | 0.32966 | 0.32966 | #N/A
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7741 | 20.7741 | 18.5 | 19.0845 | 23.3333
[16 empty] | Humidity ratio (g/gda) | 0.0028954 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049611
[16 empty] | Specific volume (L/kgda) | 821.4055 | 838.2732 | 838.2732 | 831.7876 | 833.4546 | 846.4857
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11151 | 0.34043 | 0.34043 | 0.34043 | 0.34043 | #N/A
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.8889 | 24.8642 | 24.8642 | 14.9302 | 15.5066 | 23.8889
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.013053 | 0.013053 | 0.0106 | 0.010599 | 0.011274
[16 empty] | Specific volume (L/kgda) | 872.7897 | 861.8387 | 861.8387 | 829.891 | 831.5517 | 856.6119
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11019 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | #N/A
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9309 |  | 0.58608 | 8.3488 | 0 | 0 | 0 | 6.3813 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.1972 | 29.3262 | 29.3262 | 29.9328 | 21.1111 | 21.1111 | 21.4061
| AE203 |  | 1.4649 | 0.586 | 0 | 0.85303 | 0 | 0.85303 | 32.5417 | [6 empty] | Humidity ratio (g/gda) | 0.00025894 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0016041 | 0.0023041 | 0.0023041 | 0.0023041
| AE204 |  | 2.9303 | 0.58608 | 0 | 3.5587 | 2.0648 | 5.6234 | 99.9992 | [6 empty] | Specific volume (L/kgda) | 691.8414 | 787.6103 | 858.9719 | 858.9719 | 860.6945 | 836.5805 | 836.5805 | 837.4192
| AE205 |  | 1.4642 | 0.58608 | 0 | 1.9099 | 0 | 1.9099 | 44.3101 | [6 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE206 |  | 1.4644 | 0.58608 | 0 | 1.7005 | 0.9632 | 2.6637 | 99.9992 | [6 empty] | Mass flow rate (kgda/s) | 0.11283 | 0.32966 | 0.32966 | 0.32966 | 0.32966 | #N/A | 0.21683 | 0.21683
| AE226 |  | 1.4644 | 0.58608 | 0 | 1.5568 | 1.7782 | 3.335 | 99.9992 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9741 | 20.9741 | 18.5 | 19.0845 | 23.3333 | 23.3333 | 23.6304
| AE245 |  | 1.4642 | 0.58608 | 0 | 2.202 | 0 | 2.202 | 33.8389 | [6 empty] | Humidity ratio (g/gda) | 0.0028954 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042845 | 0.0049611 | 0.0049611 | 0.0049611
[16 empty] | Specific volume (L/kgda) | 821.4055 | 838.8436 | 838.8436 | 831.7876 | 833.4546 | 846.4857 | 846.4857 | 847.3338
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11151 | 0.34043 | 0.34043 | 0.34043 | 0.34043 | #N/A | 0.22893 | 0.22893
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.8889 | 25.0648 | 25.0648 | 14.9302 | 15.5066 | 23.8889 | 23.8889 | 24.186
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.013053 | 0.013053 | 0.0106 | 0.0106 | 0.011274 | 0.011274 | 0.011274
[16 empty] | Specific volume (L/kgda) | 872.7897 | 862.4186 | 862.4186 | 829.891 | 831.5517 | 856.6119 | 856.6119 | 857.4688
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11019 | 0.34121 | 0.34121 | 0.34121 | 0.34121 | #N/A | 0.23102 | 0.23102
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.8889 | 24.0415 | 24.0415 | 18.5041 | 19.0883 | 23.3333 | 23.3333 | 23.6303
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0058499 | 0.0058499 | 0.0058499 | 0.00585 | 0.0065284 | 0.0065284 | 0.0065284
[16 empty] | Specific volume (L/kgda) | 850.243 | 849.7105 | 849.7105 | 833.8783 | 835.549 | 848.6018 | 848.6018 | 849.4517
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11123 | 0.33958 | 0.33958 | 0.33958 | 0.33958 | #N/A | 0.22835 | 0.22835
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4231 | 23.4231 | 18.5118 | 19.0951 | 23.3333 | 23.3333 | 23.6297
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.014534 | 0.014534 | 0.013367 | 0.013367 | 0.014053 | 0.014053 | 0.014053
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.6718 | 859.6718 | 843.8842 | 845.5719 | 858.7617 | 858.7617 | 859.6202
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10991 | 0.33555 | 0.33555 | 0.33555 | 0.33555 | #N/A | 0.22564 | 0.22564
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5118 | 19.0951 | 23.3333 | 23.3333 | 23.6297
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.015523 | 0.015523 | 0.013367 | 0.013367 | 0.014053 | 0.014053 | 0.014053
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.778 | 859.778 | 843.8842 | 845.5719 | 858.7617 | 858.7617 | 859.6202
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33555 | 0.33555 | 0.33555 | 0.33555 | 0.33555 | #N/A | 0.22564 | 0.22564
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 18.5025 | 19.0888 | 23.3333 | 23.3333 | 23.6304
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.005134 | 0.005134 | 0.005134
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.243 | 850.243 | 832.0238 | 833.6965 | 846.7192 | 846.7192 | 847.5674
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.34033 | 0.34033 | 0.34033 | 0.34033 | 0.34033 | #N/A | 0.22886 | 0.22886
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.9309 |  | 0.58608 | 2.3449 |  | 0.87918 | 2.9697 | 0 | 0 | 0 | 24.7328 | 7.7075 | 8.3822 | AE301 | Dry bulb temperature (°C) | -29 | 3.3982 | 7.2222 | 7.2222 | 7.7845 | 29.2883 | 27.8298 | 21.1111 | 22.2222 | 21.6708 | 21.9663
| AE303 |  | 1.4649 | 0.586 |  | 2.3449 | 0.87904 | 0 | 6.7082 | 0 | 6.7082 | 47.6873 | 2.2547 | 2.4515 |  | Humidity ratio (g/gda) | 0.00025894 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0015484 | 0.0021972 | 0.0023819 | 0.0022902 | 0.0022902
| AE304 |  | 2.9309 | 0.58608 |  | 3.5169 | 0.87918 | 0 | 10.2556 | 6.2947 | 16.5503 | 99.9992 | 0.98884 | 1.5135 |  | Specific volume (L/kgda) | 691.8414 | 785.2713 | 796.1298 | 796.1298 | 797.7263 | 858.7874 | 854.646 | 836.4373 | 839.8441 | 838.1531 | 838.9934
| AE305 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 9.3496 | 0 | 9.3496 | 65.3364 | 2.2561 | 2.4532 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE306 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 8.8688 | 5.4441 | 14.3129 | 99.9992 | 2.2588 | 2.4568 |  | Mass flow rate (kgda/s) | 0.28143 | 0.77064 | 0.77064 | 0.77064 | 0.77064 | 0.35568 | 0.41496 | #N/A | #N/A | 0.48921 | 0.48921
| AE326 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 8.3501 | 12.3442 | 20.6943 | 99.9992 | 2.2588 | 2.4568 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.9919 | 20.9919 | 12.2059 | 12.7778 | 19.1761 | 18.7408 | 23.3333 | 24.4444 | 23.8924 | 24.19
| AE345 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 9.6843 | 0 | 9.6843 | 50.7067 | 2.255 | 2.4518 |  | Humidity ratio (g/gda) | 0.0028954 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0041899 | 0.0048518 | 0.0050403 | 0.0049466 | 0.0049466
[16 empty] | Specific volume (L/kgda) | 821.4055 | 838.7678 | 838.7678 | 813.7138 | 815.3446 | 833.59 | 832.3485 | 846.3382 | 849.7654 | 848.0623 | 848.912
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27814 | 0.75399 | 0.75399 | 0.75399 | 0.75399 | 0.348 | 0.40599 | #N/A | #N/A | 0.47585 | 0.47585
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.8889 | 25.5414 | 25.5414 | 12.2065 | 12.7778 | 15.5808 | 16.4551 | 23.8889 | 25 | 24.4481 | 24.7459
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.012254 | 0.012254 | 0.008852 | 0.008852 | 0.008852 | 0.008852 | 0.0095186 | 0.0097084 | 0.0096141 | 0.0096141
[16 empty] | Specific volume (L/kgda) | 872.7897 | 862.7095 | 862.7095 | 819.774 | 821.4151 | 829.4677 | 831.9792 | 854.2369 | 857.69 | 855.9744 | 856.831
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27557 | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.34542 | 0.40299 | #N/A | #N/A | 0.47284 | 0.47284
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.8889 | 24.4471 | 24.4471 | 12.2061 | 12.7778 | 19.1778 | 18.7428 | 23.3333 | 24.4444 | 23.8924 | 24.1899
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0057551 | 0.0064187 | 0.0066076 | 0.0065137 | 0.0065137
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.7417 | 850.7417 | 815.7483 | 817.3825 | 835.6783 | 834.4349 | 848.4538 | 851.8894 | 850.1822 | 851.0336
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27745 | 0.75211 | 0.75211 | 0.75211 | 0.75211 | 0.34713 | 0.40498 | #N/A | #N/A | 0.47466 | 0.47466
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7478 | 23.7478 | 12.2065 | 12.7778 | 19.1807 | 18.747 | 23.3333 | 24.4444 | 23.8924 | 24.1897
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.011794 | 0.011794 | 0.008852 | 0.008852 | 0.008852 | 0.008852 | 0.0095189 | 0.0097087 | 0.0096144 | 0.0096144
[16 empty] | Specific volume (L/kgda) | 859.778 | 856.9076 | 856.9076 | 819.774 | 821.4151 | 839.8095 | 839.8095 | 852.6395 | 856.0923 | 854.3765 | 855.2315
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27609 | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.34542 | 0.40299 | #N/A | #N/A | 0.47233 | 0.47233
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2065 | 12.7778 | 19.1807 | 18.747 | 23.3333 | 24.4444 | 23.8924 | 24.1897
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.015523 | 0.015523 | 0.008852 | 0.008852 | 0.008852 | 0.008852 | 0.0095189 | 0.0097087 | 0.0096144 | 0.0096144
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.778 | 859.778 | 819.774 | 821.4151 | 839.8095 | 838.5636 | 852.6395 | 856.0923 | 854.3765 | 855.2315
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.74842 | 0.34542 | 0.40299 | #N/A | #N/A | 0.47233 | 0.47233
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.2059 | 12.7778 | 19.1765 | 18.7411 | 23.3333 | 24.4444 | 23.8924 | 24.19
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0051194 | 0.0053078 | 0.0052142 | 0.0052142
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.243 | 850.243 | 814.0611 | 815.6925 | 833.9468 | 832.7047 | 846.6994 | 850.1279 | 848.4242 | 849.2742
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.75367 | 0.75367 | 0.75367 | 0.75367 | 0.75367 | 0.34785 | 0.40582 | #N/A | #N/A | 0.47566 | 0.47566
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.9309 |  | 0.58608 | 2.3448 |  | 0.87918 | 10.2479 | 0 | 0 | 0 | 4.1474 | 4.4963 | 4.8725 | AE401 | Dry bulb temperature (°C) | -29 | -28.9957 | 7.2222 | 7.2222 | 7.3083 | 46.9483 | 36.0548 | 21.1111 | 22.2222
| AE403 |  | 1.4649 | 0.586 |  | 2.3449 | 0.87904 | 0 | 1.4663 | 0 | 1.4663 | 36.0086 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025894 | 0.00025911 | 0.00025911 | 0.00025911 | 0.00025861 | 0.00025861 | 0.00025861 | 0.0023034 | 0.0023096
| AE404 |  | 2.9309 | 0.58608 |  | 3.5169 | 0.87918 | 0 | 7.3735 | 5.9745 | 13.348 | 99.9992 | 0 | 0 |  | Specific volume (L/kgda) | 691.8414 | 691.8536 | 794.4835 | 794.4835 | 794.7275 | 907.0536 | 876.1849 | 836.5796 | 839.7468
| AE405 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 4.1049 | 0 | 4.1049 | 53.1717 | 0 | 0 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE406 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 3.6094 | 4.6068 | 8.2162 | 99.9992 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28143 | 0.28143 | 0.28143 | 0.28143 | 0.28143 | 0.11283 | 0.1686 | #N/A | #N/A | 0 | 0
| AE426 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87918 | 0 | 3.5586 | 5.2655 | 8.8241 | 99.9992 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9621 | 16.9621 | 12.6466 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9504 | 23.981
| AE445 |  | 1.4649 | 0.58608 |  | 2.3449 | 0.87907 | 0 | 4.1596 | 0 | 4.1596 | 49.2421 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0028954 | 0.0032519 | 0.0032519 | 0.0032519 | 0.0032519 | 0.0032519 | 0.0032519 | 0.00493 | 0.0049886 | 0.0049625 | 0.0049625
[16 empty] | Specific volume (L/kgda) | 821.4055 | 826.0373 | 826.0373 | 813.7497 | 814.1232 | 814.1236 | 814.1236 | 846.4437 | 849.6953 | 848.2496 | 848.3367
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27814 | 0.33612 | 0.33612 | 0.33612 | 0.33612 | 0.13729 | 0.19883 | #N/A | #N/A | 0.057974 | 0.057974
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.8889 | 25.91 | 25.91 | 12.4612 | 12.7778 | 12.7777 | 12.7777 | 23.8889 | 25 | 24.3794 | 24.4935
[16 empty] | Humidity ratio (g/gda) | 0.016783 | 0.01348 | 0.01348 | 0.0090036 | 0.0090036 | 0.0090036 | 0.0090036 | 0.0098953 | 0.010229 | 0.010042 | 0.010042
[16 empty] | Specific volume (L/kgda) | 872.7897 | 864.9025 | 864.9025 | 820.7028 | 821.6126 | 821.6122 | 821.6122 | 854.7464 | 858.3966 | 856.3573 | 856.6857
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27537 | 0.53988 | 0.53988 | 0.53988 | 0.53988 | 0.25821 | 0.28167 | #N/A | #N/A | 0.2645 | 0.2645
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.8889 | 24.728 | 24.728 | 12.6468 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9504 | 23.9573
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.004814 | 0.004814 | 0.004814 | 0.004814 | 0.0048143 | 0.0048143 | 0.006497 | 0.0065555 | 0.0065295 | 0.0065295
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.268 | 850.268 | 815.7831 | 816.1571 | 816.1574 | 816.1574 | 848.5594 | 851.8189 | 850.3696 | 850.3892
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27745 | 0.33516 | 0.33516 | 0.33516 | 0.33516 | 0.13689 | 0.19826 | #N/A | #N/A | 0.057705 | 0.057705
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1628 | 23.1628 | 12.6472 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9501 | 23.9568
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.014721 | 0.014721 | 0.0091159 | 0.0091159 | 0.0091159 | 0.0091159 | 0.010812 | 0.010871 | 0.010845 | 0.010845
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.169 | 859.169 | 821.3834 | 821.7587 | 821.7585 | 821.7585 | 854.3852 | 857.6675 | 856.2071 | 856.2265
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27556 | 0.33253 | 0.33253 | 0.33253 | 0.33253 | 0.13583 | 0.19671 | #N/A | #N/A | 0.056975 | 0.056975
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6472 | 12.7778 | 12.7777 | 12.7777 | 23.3333 | 24.4444 | 23.9501 | 23.9568
[16 empty] | Humidity ratio (g/gda) | 0.015523 | 0.015523 | 0.015523 | 0.0091159 | 0.0091159 | 0.0091159 | 0.0091159 | 0.010812 | 0.010871 | 0.010845 | 0.010845
[16 empty] | Specific volume (L/kgda) | 859.778 | 859.778 | 859.778 | 821.3834 | 821.7587 | 821.7585 | 821.7585 | 854.3852 | 857.6675 | 856.2071 | 856.2265
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33253 | 0.33253 | 0.33253 | 0.33253 | 0.33253 | 0.13583 | 0.19671 | #N/A | #N/A | 0.056975 | 0.056975
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.6519 | 12.7778 | 12.7778 | 12.7778 | 23.3333 | 24.4444 | 23.9504 | 23.9573
[16 empty] | Humidity ratio (g/gda) | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0044571 | 0.0061387 | 0.0061973 | 0.0061712 | 0.0061712
[16 empty] | Specific volume (L/kgda) | 850.243 | 850.243 | 850.243 | 815.3186 | 815.6925 | 815.6925 | 815.6925 | 848.0757 | 851.3333 | 849.8849 | 849.9045
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33538 | 0.33538 | 0.33538 | 0.33538 | 0.33538 | 0.13698 | 0.19839 | #N/A | #N/A | 0.057768 | 0.057768
* n/a = not applicable

## DeST
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air System Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Designer's Simulation Toolkit 2 | [5 empty] | Tsinghua University / Lawarence Berkeley National Laboratory
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | TsinghuaU-LBNL
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | DeST
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2013-11-21 |  | Model / Organization Indentifier for Charts (short): |  |  |  | DeST/TsinghuaU-LBNL
| C50..C52: | Software Name, Version, and Date of Results
| C61..J63: | Coil Loads, Fan Coil Air System, Cases AE101 - AE104
| S61..Y75: | Detailed Outputs, Fan Coil Air System, Cases AE101-AE104
| C89..J95: | Coil Loads, Single Zone Air System, Cases AE201 - AE245
| S89..Z123: | Detailed Outputs, Single Zone Air System, Cases AE201-AE245
| C137..O143: | Coil Loads, Constant Volume Terminal Reheat Air System, Cases AE301 - AE345
| S137..AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, Cases AE301-AE345
| C185..O191: | Coil Loads, Variable Air Volume Air System, Cases AE401 - AE445
| S185..AC219: | Detailed Outputs, Variable Air Volume Air System, Cases AE401-AE445
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | DeST
| Version: | 2
| Date: | 2013-11-21
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.93 |  | 0.5867 | 8.4521 | 0 | 0 | 0 | [6 empty] | AET101a | Dry bulb temperature (°C) | -29 | 4.4073 | 29.0892 | 29.0892 | 29.6791 | 21.0991 | 21.0991
| AE103 |  | 1.4666 | 0.58971 | 0 | 0.7777 | 0 | 0.7777 | 33.03 | [6 empty] | Humidity ratio (g/gda) | 0.00026 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0023324 | 0.0023324
| AE104 |  | 2.9311 | 0.58578 | 0 | 3.5428 | 2.293 | 5.8358 | 98.66 | [6 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | -28.5113 | 8.55 | 33.4266 | 33.4266 | 34.02 | 27.1262 | 27.1262
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
[15 empty] | AET103a | Dry bulb temperature (°C) | 15.5 | 20.722 | 20.722 | 18.4621 | 19.052 | 23.3479 | 23.3479
[16 empty] | Humidity ratio (g/gda) | 0.002948 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0050311 | 0.0050311
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 31.83 | 31.83 | 29.54 | 30.14 | 36.26 | 36.26
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
[15 empty] | AET104a | Dry bulb temperature (°C) | 26.9 | 24.8861 | 24.8861 | 14.7013 | 15.2912 | 23.8764 | 23.8764
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.012947 | 0.012947 | 0.010296 | 0.010296 | 0.010986 | 0.010986
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 57.97 | 57.97 | 40.79 | 41.4 | 51.94 | 51.94
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.93 |  | 0.59 | 8.3847 | 0 | 0 | 0 | [6 empty] | AET201a | Dry bulb temperature (°C) | -29 | 4.604 | 29.0892 | 29.0892 | 29.6791 | 21.099 | 21.099 | 21.3939
| AE203 |  | 1.4666 | 0.58971 | 0 | 0.84533 | 0 | 0.84533 | 33.03 | [6 empty] | Humidity ratio (g/gda) | 0.00026 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0016416 | 0.0023324 | 0.0023324 | 0.0023324
| AE204 |  | 2.9311 | 0.58578 | 0 | 3.6078 | 2.2888 | 5.8966 | 98.62 | [6 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
| AE205 |  | 1.47 | 0.59 | 0 | 1.9287 | 0 | 1.9287 | 44.81 | [6 empty] | Enthalpy (J/gda) | -28.5113 | 8.75 | 33.43 | 33.43 | 34.02 | 27.13 | 27.13 | 27.42
| AE206 |  | 1.47 | 0.59 | 0 | 1.7314 | 1.0866 | 2.8181 | 99.36 | [6 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
| AE226 |  | 1.4655 | 0.58971 | 0 | 1.593 | 2.0498 | 3.6428 | 99.65 | [5 empty] | AET203a | Dry bulb temperature (°C) | 15.5 | 20.9187 | 20.9187 | 18.4622 | 19.0521 | 23.3481 | 23.3481 | 23.643
| AE245 |  | 1.4663 | 0.58971 | 0 | 2.2158 | 0 | 2.2158 | 34.33 | [6 empty] | Humidity ratio (g/gda) | 0.002948 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0043367 | 0.0050311 | 0.0050311 | 0.0050311
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 32.02 | 32.02 | 29.54 | 30.14 | 36.26 | 36.26 | 36.56
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET204a | Dry bulb temperature (°C) | 26.9 | 25.0935 | 25.0935 | 14.7219 | 15.3118 | 23.897 | 23.897 | 24.192
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.012952 | 0.012952 | 0.010306 | 0.010306 | 0.010995 | 0.010995 | 0.011319
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 58.2 | 58.2 | 40.84 | 41.44 | 51.99 | 51.99 | 52.29
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET205a | Dry bulb temperature (°C) | 24.9 | 24.052 | 24.052 | 18.4632 | 19.0531 | 23.3479 | 23.3479 | 23.6428
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.0058987 | 0.0058987 | 0.0058987 | 0.0059 | 0.0065931 | 0.0065931 | 0.00659
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5 | 39.18 | 39.18 | 33.5 | 34.1 | 40.23 | 40.23 | 40.53
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET206a | Dry bulb temperature (°C) | 23 | 23.4067 | 23.4067 | 18.4552 | 19.0451 | 23.3378 | 23.3378 | 23.6328
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.014484 | 0.014484 | 0.013227 | 0.013227 | 0.013921 | 0.013921 | 0.013921
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 60.36 | 60.36 | 52.06 | 52.67 | 58.85 | 58.85 | 59.16
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET226a | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.4446 | 19.0345 | 23.3272 | 23.3272 | 23.6221
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.01563 | 0.01563 | 0.013257 | 0.013257 | 0.013951 | 0.013951 | 0.013951
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 62.8515 | 62.8515 | 52.13 | 52.74 | 58.92 | 58.92 | 58.92
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AET245a | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.4632 | 19.0531 | 23.3479 | 23.3479 | 23.6429
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.0052044 | 0.0052044 | 0.0052044
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.51 | 36.51 | 36.51 | 29.98 | 30.58 | 36.7 | 36.7 | 36.7
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.93 |  | 0.59 | 2.35 |  | 0.88 | 3.58 | 0 | 0 | 0 |  | 7.4721 | 8.0774 | AET301 | Dry bulb temperature (°C) | -29 | 2.3874 | 7.22 | 7.22 | 7.8099 | 29.6699 | 28.084 | 21.111 | 22.222 | 21.7092 | 22.0042
| AE303 |  | 1.4666 | 0.58971 |  | 2.3459 | 0.89087 | 0 | 6.4595 | 0 | 6.4595 | 48.22 | 2.1363 | 2.3 |  | Humidity ratio (g/gda) | 0.00026 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0015343 | 0.0022251 | 0.0024213 | 0.0023308 | 0.0023308
| AE304 |  | 2.9337 | 0.59273 |  | 3.5165 | 0.89389 | 0 | 10.0587 | 7.0108 | 17.0695 | 95.49 | 0.85904 | 1.3509 |  | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
| AE305 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 9.1806 | 0 | 9.1806 | 65.84 | 2.1367 | 2.3017 |  | Enthalpy (J/gda) | -28.5113 | 6.24 | 11.11 | 11.11 | 11.71 | 33.74 | 32.14 | 26.8658 | 28.4854 | 27.74 | 28.04
| AE306 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 8.6987 | 6.1035 | 14.8022 | 96.21 | 2.1374 | 2.3004 |  | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
| AE326 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 8.1141 | 12.8792 | 20.9933 | 98.89 | 2.1374 | 2.3005 | AET303 | Dry bulb temperature (°C) | 15.5 | 20.87 | 20.87 | 12.2049 | 12.7948 | 19.05 | 18.57 | 23.333 | 24.444 | 23.9462 | 24.2412
| AE345 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 9.4684 | 0 | 9.4684 | 51.33 | 2.1374 | 2.3005 |  | Humidity ratio (g/gda) | 0.002948 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0042354 | 0.0049298 | 0.0051345 | 0.00504 | 0.0049864
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 31.73 | 31.73 | 22.95 | 23.55 | 29.88 | 29.4 | 35.99 | 37.63 | 36.89 | 37.19
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET304 | Dry bulb temperature (°C) | 26.9 | 25.5957 | 25.5957 | 12.2047 | 12.7946 | 15.3101 | 16.1852 | 23.889 | 25 | 24.502 | 24.7969
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.012182 | 0.012182 | 0.0084426 | 0.0084426 | 0.0084426 | 0.0084426 | 0.00914 | 0.00934 | 0.0092505 | 0.0092505
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 56.75 | 56.75 | 33.56 | 34.16 | 36.73 | 37.62 | 47.2602 | 48.9046 | 48.17 | 48.47
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET305 | Dry bulb temperature (°C) | 24.9 | 24.4854 | 24.4854 | 12.2049 | 12.7948 | 19.0515 | 18.572 | 23.333 | 24.444 | 23.9462 | 24.2412
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0057974 | 0.0064918 | 0.0066965 | 0.006602 | 0.006602
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 39.36 | 39.36 | 26.89 | 27.49 | 33.84 | 33.36 | 39.96 | 41.61 | 40.86 | 41.16
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET306 | Dry bulb temperature (°C) | 23 | 23.7552 | 23.7552 | 12.1759 | 12.7658 | 19.0246 | 18.5398 | 23.333 | 24.444 | 23.9171 | 24.2121
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.011752 | 0.011752 | 0.0084916 | 0.0084916 | 0.0084916 | 0.0084916 | 0.00919 | 0.00939 | 0.0092962 | 0.009673
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 53.77 | 53.77 | 33.66 | 34.26 | 40.65 | 40.15 | 46.81 | 48.47 | 47.69 | 47.99
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2038 | 12.7937 | 19.0525 | 18.5677 | 23.333 | 24.444 | 23.9451 | 24.24
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.01563 | 0.01563 | 0.0087474 | 0.0087474 | 0.0087474 | 0.0087474 | 0.0094417 | 0.00965 | 0.009552 | 0.009552
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 62.8515 | 62.8515 | 34.33 | 34.93 | 41.32 | 40.8278 | 47.45 | 49.14 | 48.37 | 48.37
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
[15 empty] | AET345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.2049 | 12.7948 | 19.0515 | 18.572 | 23.333 | 24.444 | 23.9462 | 24.2412
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.0052044 | 0.0054091 | 0.0053146 | 0.0053146
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 36.5061 | 36.5061 | 23.64 | 24.24 | 30.55 | 30.07 | 36.68 | 38.33 | 37.59 | 37.59
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | #N/A | #N/A | 0.45307 | 0.45307
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.93 |  | 0.59 | 2.35 |  | 0.88 | 10.31 | 0 | 0 | 0 |  | 4.5019 | 4.891 | AET401 | Dry bulb temperature (°C) | -29 | -29 | 7.22 | 7.22 | 7.3073 | 46.8548 | 35.9521 | 21.111 | 22.222 | 21.7776 | 21.7776
| AE403 |  | 1.4666 | 0.58971 |  | 2.3459 | 0.89087 | 0 | 1.4433 | 0 | 1.4433 | 36.39 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.00026 | 0.0023324 | 0.0023296 | 0.0023308 | 0.0023308
| AE404 |  | 2.9337 | 0.59273 |  | 3.5165 | 0.89389 | 0 | 7.4502 | 6.5805 | 14.0307 | 97.24 | 0 | 0 |  | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
| AE405 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 4.1432 | 0 | 4.1432 | 53.52 | 0 | 0 |  | Enthalpy (J/gda) | -28.5113 | -28.5113 | 7.91 | 7.91 | 8 | 47.76 | 36.8 | 27.1382 | 28.2525 | 27.8068 | 27.8068
| AE406 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 3.6269 | 4.9686 | 8.5955 | 99.38 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.11327 | 0.1699 | #N/A | #N/A | 0 | 0
| AE426 |  | 1.4655 | 0.58971 |  | 2.3454 | 0.89087 | 0 | 3.5745 | 5.6327 | 9.2072 | 99.58 | 0 | 0 | AET403 | Dry bulb temperature (°C) | 15.5 | 16.888 | 16.888 | 12.6699 | 12.795 | 12.795 | 12.795 | 23.333 | 24.444 | 24.005 | 24.0094
| AE445 |  | 1.4663 | 0.58971 |  | 2.3442 | 0.89087 | 0 | 4.1914 | 0 | 4.1914 | 49.78 | 0 | 0 |  | Humidity ratio (g/gda) | 0.002948 | 0.00329 | 0.00329 | 0.00329 | 0.0032876 | 0.0032876 | 0.0032876 | 0.0049958 | 0.0050706 | 0.00504 | 0.00504
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 23.0316 | 25.3 | 25.3 | 21.03 | 21.16 | 21.16 | 21.16 | 36.1476 | 37.47 | 36.95 | 36.95
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.3385 | 0.3385 | 0.3385 | 0.3385 | 0.13832 | 0.20018 | #N/A | #N/A | 0.055336 | 0.055336
[15 empty] | AET404 | Dry bulb temperature (°C) | 26.9 | 25.7508 | 25.7508 | 12.4633 | 12.7916 | 12.7916 | 12.7916 | 23.889 | 25 | 24.48 | 24.5817
[16 empty] | Humidity ratio (g/gda) | 0.01685 | 0.013454 | 0.013454 | 0.0087492 | 0.0087492 | 0.0087492 | 0.0087492 | 0.0096515 | 0.0099979 | 0.0098321 | 0.0098321
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 69.9935 | 60.15 | 60.15 | 34.6 | 34.93 | 34.93 | 34.93 | 48.56 | 50.58 | 49.63 | 49.73
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.54925 | 0.54925 | 0.54925 | 0.54925 | 0.26284 | 0.28641 | #N/A | #N/A | 0.26609 | 0.26609
[15 empty] | AET405 | Dry bulb temperature (°C) | 24.9 | 24.7517 | 24.7517 | 12.6704 | 12.795 | 12.795 | 12.795 | 23.333 | 24.444 | 23.9959 | 24.0003
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.004851 | 0.004851 | 0.004851 | 0.004851 | 0.004851 | 0.004851 | 0.0065572 | 0.006633 | 0.0065986 | 0.0065986
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 37.2162 | 37.2162 | 24.97 | 25.1 | 25.1 | 25.1 | 40.1156 | 41.45 | 40.92 | 40.92
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.13829 | 0.20003 | #N/A | #N/A | 0.055153 | 0.055153
[15 empty] | AET406 | Dry bulb temperature (°C) | 23 | 23.1638 | 23.1638 | 12.6693 | 12.7939 | 12.7939 | 12.7939 | 23.333 | 24.444 | 24.0041 | 24.0085
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.014845 | 0.014845 | 0.0090684 | 0.0090684 | 0.0090684 | 0.0090684 | 0.010775 | 0.010849 | 0.010819 | 0.010819
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 61.03 | 61.03 | 35.62 | 35.74 | 35.74 | 35.74 | 50.85 | 52.18 | 51.65 | 51.65
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33835 | 0.33835 | 0.33835 | 0.33835 | 0.13822 | 0.20014 | #N/A | #N/A | 0.055191 | 0.055191
[15 empty] | AET426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6574 | 12.782 | 12.782 | 12.782 | 23.333 | 24.444 | 23.9922 | 23.9966
[16 empty] | Humidity ratio (g/gda) | 0.01563 | 0.01563 | 0.01563 | 0.0090802 | 0.0090802 | 0.0090802 | 0.0090802 | 0.010787 | 0.010861 | 0.010831 | 0.010831
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 62.8515 | 62.8515 | 62.8515 | 35.63 | 35.76 | 35.76 | 35.76 | 50.88 | 52.2078 | 51.67 | 51.67
[16 empty] | Mass flow rate (kgda/s) | 0.33835 | 0.33835 | 0.33835 | 0.33835 | 0.33835 | 0.13822 | 0.20014 | #N/A | #N/A | 0.055153 | 0.055153
[15 empty] | AET445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6704 | 12.795 | 12.795 | 12.795 | 23.333 | 24.444 | 24.0049 | 24.0093
[16 empty] | Humidity ratio (g/gda) | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.00451 | 0.0062162 | 0.006292 | 0.006261 | 0.006261
[16 empty] | Specific volume (L/kgda) | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33 | 833.33
[16 empty] | Enthalpy (J/gda) | 36.5061 | 36.5061 | 36.5061 | 24.11 | 24.24 | 24.24 | 24.24 | 39.26 | 40.58 | 40.05 | 40.06
[16 empty] | Mass flow rate (kgda/s) | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.33832 | 0.13822 | 0.20014 | #N/A | #N/A | 0.055153 | 0.055153
* n/a = not applicable

## DOE22
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | DOE-2.2 V48L | [5 empty] | National Renewable Energy Laboratory
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | NREL
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | DOE-2.2
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2015-03-12 |  | Model / Organization Indentifier for Charts (short): |  |  |  | DOE-2.2/NREL
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | DOE2.2 Design Day
| Version: | 2.2-48L
| Date: | 2015-03-12
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone |  | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible |  | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Load |  | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZsensible) |  | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh) |  | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.9307 | 0 | 0.58614 | 8.7675 | 0 | 0 | 0 | 6.4033 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.3889 | 29.2222 | 29.2222 | 29.2222 | 21.1111 | 21.1111
| AE103 | 0 | 1.4654 | 0.58614 | 0 | 0.77693 | 0 | 0.77693 | 31.6536 | [6 empty] | Humidity ratio (g/gda) | 0.0003 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0022 | 0.0022
| AE104 | 0 | 2.9307 | 0.58614 | 0 | 3.521 | 2.0119 | 5.5329 | 99.9615 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11954 | 0.35862 | 0.35862 | 0.35862 | 0.35862 | #N/A | 0.23908 |  |  | Aug 7, 2015: Zone air mass flows set to "NA" by JN
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.6889 | 21.2778 | 19 | 19 | 23.3333 | 23.3333 |  |  | Matches most recent output template.
[16 empty] | Humidity ratio (g/gda) | 0.0029 | 0.0043 | 0.0043 | 0.0043 | 0.0043 | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11241 | 0.33724 | 0.33724 | 0.33724 | 0.33724 | #N/A | 0.22483
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.8889 | 24.9056 | 25.5 | 15.2222 | 15.2222 | 23.8889 | 23.8889
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.0132 | 0.0132 | 0.0108 | 0.0108 | 0.0115 | 0.0115
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10928 | 0.32785 | 0.32785 | 0.32785 | 0.32785 | #N/A | 0.21857
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.9307 | 0 | 0.58614 | 8.7092 | 0 | 0 | 0 | 6.6125 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6111 | 28.6667 | 28.6667 | #N/A | 21.1111 | 21.1111 | 21.3889
| AE203 | 0 | 1.4654 | 0.58614 | 0 | 0.84024 | 0 | 0.84024 | 32.7731 | [6 empty] | Humidity ratio (g/gda) | 0.0003 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0022 | 0.0022 | 0.0022
| AE204 | 0 | 2.9307 | 0.58614 | 0 | 3.5901 | 2.1212 | 5.7114 | 100 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE205 | 0 | 1.4654 | 0.58614 | 0 | 1.9085 | 0 | 1.9085 | 44.8531 | [6 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE206 | 0 | 1.4654 | 0.58614 | 0 | 1.7233 | 1.0082 | 2.7314 | 99.9317 | [6 empty] | Mass flow rate (kgda/s) | 0.1197 | 0.35909 | 0.35909 | 0.35909 | 0.35909 | #N/A | 0.2394 | 0.2394
| AE226 | 0 | 1.4654 | 0.58614 | 0 | 1.5972 | 1.8077 | 3.4049 | 99.9317 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.8889 | 20.8889 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6111
| AE245 | 0 | 1.4654 | 0.58614 | 0 | 2.1878 | 0 | 2.1878 | 34.2864 | [6 empty] | Humidity ratio (g/gda) | 0.0029 | 0.0043 | 0.0043 | 0.0043 | 0.0043 | 0.005 | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11256 | 0.33768 | 0.33768 | 0.33768 | 0.33768 | #N/A | 0.22512 | 0.22512
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.8889 | 25.1111 | 25.1111 | 14.6111 | #N/A | 23.8889 | 23.8889 | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.013 | 0.013 | 0.0104 | 0.0104 | 0.0111 | 0.0111 | 0.0111
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10948 | 0.32843 | 0.32843 | 0.32843 | 0.32843 | #N/A | 0.21895 | 0.21895
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.8889 | 24.0556 | 24.0556 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0059 | 0.0059 | 0.0059 | 0.0059 | 0.0066 | 0.0066 | 0.0066
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11109 | 0.33327 | 0.33327 | 0.33327 | 0.33327 | #N/A | 0.22218 | 0.22218
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4444 | 23.4444 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6111
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0145 | 0.0145 | 0.0133 | 0.0133 | 0.014 | 0.014 | 0.014
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.10983 | 0.32948 | 0.32948 | 0.32948 | 0.32948 | #N/A | 0.21965 | 0.21965
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6667
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0156 | 0.0156 | 0.0133 | 0.0133 | 0.0141 | 0.0141 | 0.0141
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.32941 | #N/A | 0.21961 | 0.21961
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 18.4444 | #N/A | 23.3333 | 23.3333 | 23.6667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0052 | 0.0052 | 0.0052
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33309 | 0.33309 | 0.33309 | 0.33309 | 0.33309 | #N/A | 0.22206 | 0.22206
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | -2.9307 | 0 | 0.58614 | -2.3446 | 0 | 0.87921 | 3.7882 | 0 | 0 | 0 | 23.9613 | 7.706 | 8.3763 | AE301 | Dry bulb temperature (°C) | -29 | #N/A | 7.2222 | 7.2222 | 7.7778 | #N/A | #N/A | 21.1111 | 22.2222 | #N/A | 21.9444
| AE303 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 6.4197 | 0 | 6.4197 | 47.9247 | 2.15 | 2.3194 |  | Humidity ratio (g/gda) | 0.0003 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | #N/A | #N/A | 0.0022 | 0.0022
| AE304 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 9.8897 | 6.214 | 16.1037 | 100 | 0.79774 | 1.2681 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE305 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.9287 | 0 | 8.9287 | 65.5319 | 2.0723 | 2.2232 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE306 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.5975 | 5.4338 | 14.0314 | 100 | 2.1107 | 2.2695 |  | Mass flow rate (kgda/s) | 0.29649 | 0.77088 | 0.77088 | 0.77088 | 0.77088 | 0.35579 | 0.41509 | #N/A | #N/A | 0.47438 | 0.47438
| AE326 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 8.2315 | 11.7123 | 19.9438 | 100 | 2.1256 | 2.2886 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8333 | 20.8333 | 12.1667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.2222
| AE345 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 9.2851 | 0 | 9.2851 | 51.1359 | 2.0887 | 2.2414 |  | Humidity ratio (g/gda) | 0.0029 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | 0.0042 | #N/A | #N/A | 0.005 | 0.005
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28151 | 0.73193 | 0.73193 | 0.73193 | 0.73193 | 0.33781 | 0.39412 | #N/A | #N/A | 0.45042 | 0.45042
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.8889 | 25.5556 | 25.5556 | 12.2222 | 12.8333 | #N/A | #N/A | 23.8889 | 25 | #N/A | 24.7222
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.0124 | 0.0124 | 0.0089 | 0.0089 | 0.0089 | 0.0089 | #N/A | #N/A | 0.0097 | 0.0097
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.2735 | 0.71109 | 0.71109 | 0.71109 | 0.71109 | 0.32819 | 0.38289 | #N/A | #N/A | 0.43759 | 0.43759
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.8889 | 24.4444 | 24.4444 | 12.2778 | 12.8889 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | #N/A | #N/A | 0.0066 | 0.0066
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27741 | 0.72126 | 0.72126 | 0.72126 | 0.72126 | 0.33289 | 0.38837 | #N/A | #N/A | 0.44385 | 0.44385
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7222 | 23.7222 | 12.2222 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.012 | 0.012 | 0.0089 | 0.0089 | 0.0089 | 0.0089 | #N/A | #N/A | 0.0097 | 0.0097
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27538 | 0.716 | 0.716 | 0.716 | 0.716 | 0.33046 | 0.38554 | n/a* | n/a* | 0.44061 | 0.44061
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2222 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0156 | 0.0156 | 0.0089 | 0.0089 | 0.0089 | 0.0089 | #N/A | #N/A | 0.0097 | 0.0097
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.71372 | 0.71372 | 0.71372 | 0.71372 | 0.71372 | 0.32941 | 0.38431 | #N/A | #N/A | 0.43921 | 0.43921
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.2222 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 24.1667
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | #N/A | #N/A | 0.0053 | 0.0053
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.72169 | 0.72169 | 0.72169 | 0.72169 | 0.72169 | 0.33309 | 0.3886 | #N/A | #N/A | 0.44412 | 0.44412
* =na()
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | -2.9307 | 0 | 0.58614 | -2.3446 | 0 | 0.87921 | 10.8176 | 0 | 0 | 0 | 4.8015 | 4.5839 | 5.0147 | AE401 | Dry bulb temperature (°C) | -29 | -17.7778 | 7.2222 | 7.2222 | 7.2778 | #N/A | #N/A | 21.1111 | 22.2222 | #N/A | #N/A | 40
| AE403 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 1.4021 | 0 | 1.4021 | 34.2896 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | #N/A | #N/A | #N/A | #N/A
| AE404 | 0 | 2.9307 | 0.58614 | 0 | 3.5169 | 0.87921 | 0 | 7.4587 | 5.9168 | 13.3755 | 100 | 0 | 0 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE405 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1138 | 0 | 4.1138 | 51.8548 | 0 | 0 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE406 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6801 | 4.4948 | 8.1749 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.29707 | 0.29707 | 0.29707 | 0.29707 | 0.29707 | 0.11883 | 0.17824 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 3.6423 | 5.1885 | 8.8308 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7778 | 16.7778 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | 7.6667
| AE445 | 0 | 1.4654 | 0.58614 | 0 | 2.3446 | 0.87921 | 0 | 4.1701 | 0 | 4.1701 | 49.664 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | #N/A | #N/A | 0.0041 | 0.0041
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28597 | 0.33688 | 0.33688 | 0.33688 | 0.33688 | 0.13784 | 0.19904 | #N/A | #N/A | 0.050903 | 0.050903
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.8889 | 25.7222 | 25.7222 | 12.4444 | 12.7778 | #N/A | #N/A | 23.8889 | 25 | #N/A | 24.5 | -0.72222
[16 empty] | Humidity ratio (g/gda) | 0.0168 | 0.0135 | 0.0135 | 0.009 | 0.009 | 0.009 | 0.009 | #N/A | #N/A | 0.0101 | 0.0101
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27289 | 0.53541 | 0.53541 | 0.53541 | 0.53541 | 0.25542 | 0.27998 | #N/A | #N/A | 0.26252 | 0.26252
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.8889 | 24.7222 | 24.7222 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | -0.27778
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | #N/A | #N/A | 0.0059 | 0.0059
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27761 | 0.33591 | 0.33591 | 0.33591 | 0.33591 | 0.13714 | 0.19877 | #N/A | #N/A | 0.058299 | 0.058299
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1667 | 23.1667 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | 1.2778
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0147 | 0.0147 | 0.0092 | 0.0092 | 0.0092 | 0.0092 | #N/A | #N/A | 0.0103 | 0.0103
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.27474 | 0.32968 | 0.32968 | 0.32968 | 0.32968 | 0.13462 | 0.19506 | #N/A | #N/A | 0.054947 | 0.054947
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | 1.4444
[16 empty] | Humidity ratio (g/gda) | 0.0156 | 0.0156 | 0.0156 | 0.0092 | 0.0092 | 0.0092 | 0.0092 | #N/A | #N/A | 0.0104 | 0.0104
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.32941 | 0.13451 | 0.1949 | #N/A | #N/A | 0.054902 | 0.054902
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.8889 | 24.8889 | 24.8889 | 12.6667 | 12.7778 | #N/A | #N/A | 23.3333 | 24.4444 | #N/A | 23.9444 | -0.44444
[16 empty] | Humidity ratio (g/gda) | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | 0.0045 | #N/A | #N/A | 0.0057 | 0.0057
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33586 | 0.33586 | 0.33586 | 0.33586 | 0.33586 | 0.13712 | 0.19874 | #N/A | #N/A | 0.05829 | 0.05829
* =na()

## Eplus
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air System Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | EnergyPlus 8.2.0 | [5 empty] | GARD Analytics
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | GARD
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | EnergyPlus
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2015-01-14 |  | Model / Organization Indentifier for Charts (short): |  |  |  | EnergyPlus/GARD
| C50..C52: | Software Name, Version, and Date of Results
| C61..J63: | Coil Loads, Fan Coil Air System, Cases AE101 - AE104
| S61..Y75: | Detailed Outputs, Fan Coil Air System, Cases AE101-AE104
| C89..J95: | Coil Loads, Single Zone Air System, Cases AE201 - AE245
| S89..Z123: | Detailed Outputs, Single Zone Air System, Cases AE201-AE245
| C137..O143: | Coil Loads, Constant Volume Terminal Reheat Air System, Cases AE301 - AE345
| S137..AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, Cases AE301-AE345
| C185..O191: | Coil Loads, Variable Air Volume Air System, Cases AE401 - AE445
| S185..AC219: | Detailed Outputs, Variable Air Volume Air System, Cases AE401-AE445
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | EnergyPlus
| Version: | 8.2.0
| Date: | 2015-01-14
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | -2.931 |  | 0.5861 | 8.4534 | 0 | 0 | 0 | 6.5151 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4539 | 29.0494 | 29.0494 | 29.6355 | 21.1183 | 21.1183
| AE103 |  | 1.465 | 0.5861 | 0 | 0.76554 | 0 | 0.76554 | 32.5142 | [6 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0022887 | 0.0022887
| AE104 |  | 2.931 | 0.5861 | 0 | 3.4986 | 2.1742 | 5.6728 | 99.6158 | [6 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | -28.5066 | 8.5207 | 33.309 | 33.309 | 33.8997 | 27.0344 | 27.0344
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.726 | 20.726 | 18.5095 | 19.0928 | 23.3293 | 23.3293
[16 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049599 | 0.0049599
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.7063 | 31.7063 | 29.4615 | 30.0522 | 36.0616 | 36.0616
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8949 | 24.8949 | 14.9265 | 15.5032 | 23.8823 | 23.8823
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013079 | 0.013079 | 0.010558 | 0.010558 | 0.011233 | 0.011233
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 58.3316 | 58.3316 | 41.6971 | 42.2878 | 52.5907 | 52.5907
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | -2.931 |  | 0.5861 | 8.387 | 8.048e-08 | 1.8383e-05 | 1.8464e-05 | 6.5149 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6476 | 29.0498 | 29.0498 | 29.6359 | 21.1187 | 21.1187 | 21.4084
| AE203 |  | 1.465 | 0.5861 | 0 | 0.83269 | 0 | 0.83269 | 32.5148 | [6 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0022887 | 0.0022887 | 0.0022887
| AE204 |  | 2.931 | 0.5861 | 0 | 3.5657 | 2.1735 | 5.7392 | 99.6397 | [6 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
| AE205 |  | 1.465 | 0.5861 | 0 | 1.9127 | 0 | 1.9127 | 44.111 | [6 empty] | Enthalpy (J/gda) | -28.5066 | 8.7159 | 33.3094 | 33.3094 | 33.9001 | 27.0348 | 27.0348 | 27.3272
| AE206 |  | 1.465 | 0.5861 | 0 | 1.6967 | 1.0417 | 2.7383 | 99.0255 | [6 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
| AE226 |  | 1.465 | 0.5861 | 0 | 1.5548 | 1.8634 | 3.4182 | 99.8073 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9201 | 20.9201 | 18.5093 | 19.0925 | 23.3288 | 23.3288 | 23.6201
| AE245 |  | 1.465 | 0.5861 | 0 | 2.2073 | 0 | 2.2073 | 33.9915 | [6 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049599 | 0.0049599 | 0.0049599
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.9029 | 31.9029 | 29.4612 | 30.0519 | 36.0611 | 36.0611 | 36.3565
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.0862 | 25.0862 | 14.9264 | 15.5031 | 23.8822 | 23.8822 | 24.1702
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013081 | 0.013081 | 0.010561 | 0.010561 | 0.011236 | 0.011236 | 0.011236
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 58.5327 | 58.5327 | 41.7033 | 42.2941 | 52.5969 | 52.5969 | 52.8923
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0456 | 24.0456 | 18.5236 | 19.1052 | 23.3296 | 23.3296 | 23.62
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.005832 | 0.005832 | 0.005832 | 0.005832 | 0.0065075 | 0.0065075 | 0.0065075
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 39.0081 | 39.0081 | 33.3995 | 33.9902 | 39.9994 | 39.9994 | 40.2948
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4106 | 23.4106 | 18.5888 | 19.1626 | 23.33 | 23.33 | 23.6165
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.014507 | 0.014507 | 0.013302 | 0.013302 | 0.013978 | 0.013978 | 0.013978
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 60.4363 | 60.4363 | 52.4066 | 52.9973 | 59.0066 | 59.0066 | 59.302
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5897 | 19.1634 | 23.33 | 23.33 | 23.6164
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.015565 | 0.015565 | 0.01341 | 0.01341 | 0.014086 | 0.014086 | 0.014086
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 62.7048 | 62.7048 | 52.6815 | 53.2723 | 59.2816 | 59.2816 | 59.5769
[16 empty] | Mass flow rate (kgda/s) | 0.34102 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5115 | 19.0946 | 23.3294 | 23.3294 | 23.6205
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051565 | 0.0051565 | 0.0051565
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 36.4346 | 36.4346 | 29.962 | 30.5528 | 36.562 | 36.562 | 36.8573
[16 empty] | Mass flow rate (kgda/s) | 0.34102 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.22735 | 0.22735
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | -2.931 |  | 0.5861 | -2.345 |  | 0.8792 | 3.5747 | 0 | 0 | 0 | 23.8906 | 7.5057 | 8.1309 | AE301 | Dry bulb temperature (°C) | -29 | 2.4185 | 7.22 | 7.22 | 7.8063 | 29.649 | 28.0886 | 21.1299 | 22.2485 | 21.6893 | 21.982
| AE303 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 6.4764 | 0 | 6.4764 | 47.4569 | 2.1827 | 2.3607 |  | Humidity ratio (g/gda) | 0.00025901 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0014957 | 0.0021723 | 0.0023649 | 0.0022686 | 0.0022686
| AE304 |  | 2.931 | 0.5861 |  | 3.517 | 0.8792 | 0 | 10.1563 | 6.6217 | 16.778 | 99.1258 | 0.94208 | 1.4552 |  | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
| AE305 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 9.1994 | 0 | 9.1994 | 64.909 | 2.193 | 2.3739 |  | Enthalpy (J/gda) | -28.5066 | 6.1776 | 11.0156 | 11.0156 | 11.6064 | 33.6155 | 32.0433 | 26.7502 | 28.3684 | 27.5593 | 27.8547
| AE306 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 8.7437 | 5.7489 | 14.4926 | 99.2475 | 2.2136 | 2.4005 |  | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
| AE326 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 8.2481 | 12.5316 | 20.7797 | 99.9275 | 2.2141 | 2.4012 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8531 | 20.8531 | 12.197 | 12.7804 | 19.1013 | 18.6401 | 23.3385 | 24.4517 | 23.8952 | 24.1865
| AE345 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 9.5096 | 0 | 9.5096 | 50.9944 | 2.1849 | 2.3635 |  | Humidity ratio (g/gda) | 0.0029334 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0041681 | 0.0048436 | 0.0050359 | 0.0049397 | 0.0049397
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.5397 | 31.5397 | 22.7746 | 23.3653 | 29.7658 | 29.2989 | 35.775 | 37.3934 | 36.5842 | 36.8796
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5756 | 7.22 | 12.2012 | 12.7797 | 15.485 | 16.3615 | 23.8914 | 25.0047 | 24.4481 | 24.737
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.012324 | 0.012324 | 0.0087725 | 0.0087725 | 0.0087725 | 0.0087725 | 0.0094477 | 0.00964 | 0.0095439 | 0.0095439
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 57.1062 | 57.1062 | 34.3988 | 34.9895 | 37.752 | 38.6471 | 48.0548 | 49.6829 | 48.8688 | 49.1642
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4598 | 7.22 | 12.1989 | 12.7806 | 19.1133 | 18.6566 | 23.3385 | 24.4517 | 23.8952 | 24.1857
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0057157 | 0.0063912 | 0.0065835 | 0.0064873 | 0.0064873
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 39.1326 | 39.1326 | 26.6821 | 27.2729 | 33.7034 | 33.2397 | 39.7127 | 41.3343 | 40.5235 | 40.8188
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7256 | 7.22 | 12.2019 | 12.7804 | 19.1369 | 18.6889 | 23.3385 | 24.4517 | 23.8952 | 24.1841
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.011867 | 0.011867 | 0.0087839 | 0.0087839 | 0.0087839 | 0.0087839 | 0.0094593 | 0.0096517 | 0.0095555 | 0.0095555
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 54.0424 | 54.0424 | 34.4281 | 35.0189 | 41.5099 | 41.0525 | 47.5192 | 49.1471 | 48.3331 | 48.6285
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 7.22 | 12.2017 | 12.7801 | 19.1373 | 18.6896 | 23.3385 | 24.4517 | 23.8952 | 24.184
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.015565 | 0.015565 | 0.0088448 | 0.0088448 | 0.0088448 | 0.0088448 | 0.0095202 | 0.0097126 | 0.0096164 | 0.0096164
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 62.7048 | 62.7048 | 34.5816 | 35.1723 | 41.6648 | 41.2075 | 47.6741 | 49.3022 | 48.4881 | 48.7835
[16 empty] | Mass flow rate (kgda/s) | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 7.22 | 12.197 | 12.78 | 19.1037 | 18.6434 | 23.3385 | 24.4517 | 23.8952 | 24.1863
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0051565 | 0.0053488 | 0.0052527 | 0.0052527
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 36.4346 | 36.4346 | 23.5643 | 24.155 | 30.562 | 30.0957 | 36.5712 | 38.1903 | 37.3807 | 37.6761
[16 empty] | Mass flow rate (kgda/s) | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.4547 | 0.4547
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | -2.931 |  | 0.5861 | -2.345 |  | 0.8792 | 10.343 | 0 | 0 | 0 | 4.1501 | 4.5034 | 4.9022 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.22 | 7.2031 | 7.2901 | 46.6969 | 35.8886 | 21.1452 | 22.2593 | 21.1452 | 21.1452
| AE403 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 1.3987 | 0 | 1.3987 | 35.8492 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.00025901 | 0.0022887 | 0.0022872 | 0.0022887 | 0.0022887
| AE404 |  | 2.931 | 0.5861 |  | 3.517 | 0.8792 | 0 | 7.3706 | 6.3173 | 13.6879 | 98.7059 | 0 | 0 |  | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| AE405 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 4.0977 | 0 | 4.0977 | 52.7786 | 0 | 0 |  | Enthalpy (J/gda) | -28.5066 | -28.5066 | 7.8892 | 7.8892 | 7.9766 | 47.5931 | 36.7273 | 27.0614 | 28.1819 | 27.0614 | 27.0614
| AE406 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 3.5834 | 4.84 | 8.4235 | 99.7649 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28418 | 0.28418 | 0.28418 | 0.28418 | 0.28418 | 0.11367 | 0.17051 | n/a* | n/a* | 0 | 0
| AE426 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 3.5416 | 5.3897 | 8.9313 | 99.9528 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7888 | 7.22 | 12.6598 | 12.78 | 12.78 | 12.78 | 23.3441 | 24.4608 | 23.9508 | 23.9546
| AE445 |  | 1.465 | 0.5861 |  | 2.345 | 0.8792 | 0 | 4.1451 | 0 | 4.1451 | 49.4632 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029334 | 0.003241 | 0.003241 | 0.003241 | 0.003241 | 0.003241 | 0.003241 | 0.0049254 | 0.0049851 | 0.0049578 | 0.0049578
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 25.0767 | 25.0767 | 20.9029 | 21.0244 | 21.0244 | 21.0244 | 35.9889 | 37.2733 | 36.6866 | 36.6905
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.3351 | 0.3351 | 0.3351 | 0.3351 | 0.13676 | 0.19796 | n/a* | n/a* | 0.050546 | 0.050919
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.7623 | 7.22 | 12.4725 | 12.7797 | 12.7808 | 12.7808 | 23.9001 | 25.0168 | 24.3846 | 24.4749
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013543 | 0.013543 | 0.0088944 | 0.0088944 | 0.0088944 | 0.0088944 | 0.009788 | 0.010124 | 0.0099335 | 0.0099335
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 60.4045 | 60.4045 | 34.9834 | 35.2972 | 35.2982 | 35.2982 | 48.93 | 50.9269 | 49.7961 | 49.8885
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.53845 | 0.53845 | 0.53845 | 0.53845 | 0.25766 | 0.28079 | n/a* | n/a* | 0.25427 | 0.25427
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.758 | 7.22 | 12.661 | 12.7802 | 12.7802 | 12.7802 | 23.3441 | 24.4607 | 23.9497 | 23.9534
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0047837 | 0.0064728 | 0.0065327 | 0.0065053 | 0.0065053
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 37.0618 | 37.0618 | 24.7987 | 24.9195 | 24.9195 | 24.9195 | 39.9261 | 41.2141 | 40.6246 | 40.6284
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.33415 | 0.33415 | 0.33415 | 0.33415 | 0.13638 | 0.19741 | n/a* | n/a* | 0.049606 | 0.049969
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1345 | 7.22 | 12.6637 | 12.78 | 12.7899 | 12.7899 | 23.3441 | 24.4607 | 23.9468 | 23.95
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.014891 | 0.014891 | 0.0091064 | 0.0091064 | 0.0091018 | 0.0091018 | 0.010803 | 0.010863 | 0.010835 | 0.010835
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 61.1277 | 61.1277 | 35.7139 | 35.8327 | 35.8312 | 35.8312 | 50.9427 | 52.2412 | 51.6436 | 51.6468
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.33145 | 0.33145 | 0.33145 | 0.33145 | 0.13543 | 0.19602 | n/a* | n/a* | 0.047271 | 0.047271
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 7.22 | 12.6638 | 12.7801 | 12.79 | 12.79 | 23.3441 | 24.4607 | 23.9468 | 23.9499
[16 empty] | Humidity ratio (g/gda) | 0.015565 | 0.015565 | 0.015565 | 0.0091238 | 0.0091238 | 0.009124 | 0.009124 | 0.010825 | 0.010885 | 0.010858 | 0.010858
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 62.7048 | 62.7048 | 62.7048 | 35.758 | 35.8769 | 35.8875 | 35.8875 | 50.9995 | 52.2981 | 51.7004 | 51.7036
[16 empty] | Mass flow rate (kgda/s) | 0.33144 | 0.33144 | 0.33144 | 0.33144 | 0.33144 | 0.13543 | 0.19601 | n/a* | n/a* | 0.047261 | 0.047261
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 7.22 | 12.6608 | 12.7802 | 12.7802 | 12.7802 | 23.3441 | 24.4607 | 23.9499 | 23.9536
[16 empty] | Humidity ratio (g/gda) | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.004481 | 0.0061691 | 0.006229 | 0.0062016 | 0.0062016
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 36.4346 | 36.4346 | 36.4346 | 24.0343 | 24.1552 | 24.1552 | 24.1552 | 39.1535 | 40.4408 | 39.8519 | 39.8557
[16 empty] | Mass flow rate (kgda/s) | 0.33427 | 0.33427 | 0.33427 | 0.33427 | 0.33427 | 0.13645 | 0.19752 | n/a* | n/a* | 0.049791 | 0.050091
* n/a = not applicable
EnergyPlus 4-Pipe Fan Coil
| Last Hour of Simulation - Summary Outputs - Fan Coil Air System | [13 empty] | EnergyPlus 4-Pipe Fan Coil
|  | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZsensible) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AET101a | -2.931 | 0.5861 | 8.4527 | 0 | 0 | 0 | 29.9418 | [6 empty] | AET101a | Dry bulb temperature (°C) | -29 | 4.4496 | 29.6291 | 5.0358 | 29.6291 | 21.1119 | 21.1119
| AET103a | 1.465 | 0.5861 | 0 | 0.76509 | 0 | 0.76509 | 31.3427 | [7 empty] | Humidity ratio (g/gda) | 0.00025901 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0016122 | 0.0022888 | 0.0022888
| AET104a | 2.931 | 0.5861 | 0 | 3.4965 | 2.1082 | 5.6047 | 98.0115 | [7 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | -28.5066 | 8.5164 | 33.8933 | 9.1072 | 33.8933 | 27.0279 | 27.0279
| Notes: | [14 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
| 1) EnergyPlus 4-Pipe Fan Coil model only allows a blow-through configuration with the heating coil placed after the cooling coil | [13 empty] | AET103a | Dry bulb temperature (°C) | 15.5 | 20.7283 | 19.0965 | 19.0965 | 19.0965 | 23.3328 | 23.3328
| 2) Outdoor air and exhaust air interchange takes place automatically within the fan coil unit without the aid of an exhaust fan | [14 empty] | Humidity ratio (g/gda) | 0.0029334 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0042844 | 0.0049598 | 0.0049598
| and therefore the fan coil return air flow rate is always equal to the supply air flow rate | [14 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 22.9958 | 31.7087 | 30.0559 | 30.0559 | 30.0559 | 36.0651 | 36.0651
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
[15 empty] | AET104a | Dry bulb temperature (°C) | 26.9 | 24.8985 | 15.5126 | 15.5126 | 15.5126 | 23.8882 | 23.8882
[16 empty] | Humidity ratio (g/gda) | 0.016772 | 0.013235 | 0.010791 | 0.010791 | 0.010791 | 0.011466 | 0.011466
[16 empty] | Specific volume (L/kgda) | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519 | 830.3519
[16 empty] | Enthalpy (J/gda) | 69.8136 | 58.7307 | 42.8864 | 42.8864 | 42.8864 | 53.1892 | 53.1892
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
* n/a = not applicable

## IES-VE
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Integrated Environmental Solutions Virtual Environment IES-VE 2014.2 | [5 empty] | Integrated Environmental Solutions
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | IES
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | IES-VE
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2015-02-20 |  | Model / Organization Indentifier for Charts (short): |  |  |  | IES-VE/IES
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | IES-VE
| Version: | <VE>2014.2
| Date: | 2015-02-20
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.931 | 0 | 0.5861 | 8.513 | 0 | 0 | 0 | 6.75 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4073 | 28.994 | 28.994 | 29.5758 | 21.111 | 21.111
| AE103 | 0 | 1.465 | 0.5861 | 0 | 0.762 | 0 | 0.762 | 32.91 | [6 empty] | Humidity ratio (g/gda) | 0.000262 | 0.00167 | 0.00167 | 0.00167 | 0.00167 | 0.00237 | 0.002374
| AE104 | 0 | 2.931 | 0.5861 | 0 | 3.48 | 2.127 | 5.607 | 100 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 |  | Aug 7, 2015: Zone air mass flows set to "NA" by JN
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7214 | 20.7214 | 18.5195 | 19.1013 | 23.3321 | 23.3321 |  | Matches most recent output template.
[16 empty] | Humidity ratio (g/gda) | 0.002947 | 0.004355 | 0.004355 | 0.004355 | 0.004355 | 0.005059 | 0.005059
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8934 | 24.8934 | 14.8437 | 15.4255 | 23.8901 | 23.8901
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.013136 | 0.013136 | 0.010581 | 0.010581 | 0.011285 | 0.011285
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.931 | 0 | 0.5861 | 8.446 | 0 | 0 | 0 | 6.75 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6011 | 28.9937 | 28.9937 | 29.5755 | 21.1107 | 21.1107 | 21.4016
| AE203 | 0 | 1.465 | 0.5861 | 0 | 0.83 | 0 | 0.83 | 32.91 | [6 empty] | Humidity ratio (g/gda) | 0.000262 | 0.00167 | 0.00167 | 0.00167 | 0.00167 | 0.002374 | 0.002374 | 0.002374
| AE204 | 0 | 2.931 | 0.5861 | 0 | 3.547 | 2.128 | 5.675 | 100 | [6 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE205 | 0 | 1.465 | 0.5861 | 0 | 1.915 | 0 | 1.915 | 44.59 | [6 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE206 | 0 | 1.465 | 0.5861 | 0 | 1.695 | 1 | 2.696 | 100 | [6 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
| AE226 | 0 | 1.465 | 0.5861 | 0 | 1.552 | 1.825 | 3.377 | 100 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9148 | 20.9148 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
| AE245 | 0 | 1.564 | 0.5861 | 0 | 2.21 | 0 | 2.21 | 34.06 | [6 empty] | Humidity ratio (g/gda) | 0.002947 | 0.004355 | 0.004355 | 0.004355 | 0.004355 | 0.005059 | 0.005059 | 0.005059
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.0861 | 25.0861 | 14.8418 | 15.4236 | 23.8882 | 23.8882 | 24.1791
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.013135 | 0.013135 | 0.01058 | 0.01058 | 0.011284 | 0.011284 | 0.011284
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0481 | 24.0481 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.005916 | 0.005916 | 0.005916 | 0.005916 | 0.00662 | 0.00662 | 0.00662
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4148 | 23.4148 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.014624 | 0.014624 | 0.013424 | 0.013424 | 0.014128 | 0.014128 | 0.014128
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.015616 | 0.015616 | 0.013424 | 0.013424 | 0.014128 | 0.014128 | 0.014128
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5187 | 19.1005 | 23.3313 | 23.3313 | 23.6222
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.005212 | 0.005212 | 0.005212
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
* n/a = not applicable
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 3.647 | 0 | 0 | 0 | 24.65 | 7.539 | 8.17 | AE301 | Dry bulb temperature (°C) | -29 | 2.3582 | 7.22 | 7.22 | 7.8018 | 29.5754 | 28.026 | 21.1106 | 22.221 | 21.6658 | 21.9567
| AE303 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 6.483 | 0 | 6.483 | 48.02 | 2.188 | 2.366 |  | Humidity ratio (g/gda) | 0.000262 | 0.001549 | 0.001549 | 0.001549 | 0.001549 | 0.001549 | 0.001549 | 0.002253 | 0.002454 | 0.002354 | 0.002354
| AE304 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 10.034 | 6.629 | 16.662 | 100 | 0.915 | 1.419 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE305 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.195 | 0 | 9.195 | 65.57 | 2.188 | 2.366 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE306 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.652 | 5.75 | 14.403 | 100 | 2.188 | 2.366 |  | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
| AE326 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.096 | 12.558 | 20.654 | 100 | 2.188 | 2.366 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.8401 | 20.8401 | 12.199 | 12.7808 | 19.1006 | 18.637 | 23.3314 | 24.442 | 23.8867 | 24.1776
| AE345 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.529 | 0 | 9.529 | 51.1 | 2.188 | 2.366 |  | Humidity ratio (g/gda) | 0.002947 | 0.004234 | 0.004234 | 0.004234 | 0.004234 | 0.004234 | 0.004234 | 0.004938 | 0.005139 | 0.005039 | 0.005039
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5681 | 25.5681 | 12.199 | 12.7808 | 15.4247 | 16.2939 | 23.8893 | 25.001 | 24.4447 | 24.7356
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.012443 | 0.012443 | 0.008891 | 0.008891 | 0.008891 | 0.008891 | 0.009595 | 0.009796 | 0.009695 | 0.009695
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4554 | 24.4554 | 12.199 | 12.7808 | 19.1006 | 18.6371 | 23.3314 | 24.4419 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.005795 | 0.005795 | 0.005795 | 0.005795 | 0.005795 | 0.005795 | 0.006499 | 0.0067 | 0.0066 | 0.0066
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7247 | 23.7247 | 12.199 | 12.7808 | 19.1006 | 18.6371 | 23.3314 | 24.4419 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.011971 | 0.011971 | 0.008888 | 0.008888 | 0.008888 | 0.008888 | 0.009592 | 0.009793 | 0.009693 | 0.009693
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.199 | 12.7808 | 19.1006 | 18.637 | 23.3314 | 24.442 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.015616 | 0.015616 | 0.008909 | 0.008909 | 0.008909 | 0.008909 | 0.009613 | 0.009814 | 0.009713 | 0.009713
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.199 | 12.7808 | 19.1006 | 18.6371 | 23.3314 | 24.4419 | 23.8867 | 24.1776
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.005212 | 0.005413 | 0.005312 | 0.005312
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.73624 | 0.3398 | 0.39643 | 0.3398 | 0.39643 | 0.45307 | 0.45307
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 10.451 | 0 | 0 | 0 | 4.17 | 4.524 | 4.926 | AE401 | Dry bulb temperature (°C) | -29 | -29 | 7.22 | 7.22 | 7.3103 | 46.5047 | 35.7662 | 21.1103 | 22.2208 | #N/A | #N/A
| AE403 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 1.399 | 0 | 1.399 | 35.98 | 0 | 0 |  | Humidity ratio (g/gda) | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.000262 | 0.002374 | 0.002374 | #N/A | #N/A
| AE404 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 7.333 | 6.313 | 13.645 | 100 | 0 | 0 |  | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE405 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.111 | 0 | 4.111 | 53.05 | 0 | 0 |  | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| AE406 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.567 | 4.868 | 8.435 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.28316 | 0.11327 | 0.1699 | 0.11327 | 0.1699 | 0 | 0
| AE426 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.516 | 5.456 | 8.972 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7759 | 16.7759 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9482
| AE445 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.16 | 0 | 4.16 | 49.58 | 0 | 0 |  | Humidity ratio (g/gda) | 0.002947 | 0.003265 | 0.003265 | 0.00326 | 0.003265 | 0.003265 | 0.003265 | 0.005021 | 0.005084 | 0.005037 | 0.005055
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | 0.13624 | 0.1973 | 0.05055 | 0.05037
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.744 | 25.744 | 12.47 | 12.7846 | 12.7846 | 12.7846 | 23.8934 | 25.0043 | 24.3776 | 24.4762
[16 empty] | Humidity ratio (g/gda) | 0.016839 | 0.013639 | 0.013639 | 0.009056 | 0.009056 | 0.009056 | 0.009056 | 0.00998 | 0.010327 | 0.010131 | 0.010131
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.54137 | 0.54137 | 0.54137 | 0.54137 | 0.25892 | 0.28245 | 0.25892 | 0.28245 | 0.25821 | 0.25821
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7562 | 24.7562 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9482
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004826 | 0.004826 | 0.00482 | 0.004826 | 0.004826 | 0.004826 | 0.006582 | 0.006645 | 0.006616 | 0.006616
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | 0.13624 | 0.1973 | 0.05037 | 0.05037
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1432 | 23.1432 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4432 | 23.9365 | 23.9482
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.014914 | 0.014914 | 0.009175 | 0.009175 | 0.009175 | 0.009175 | 0.010931 | 0.010994 | 0.010966 | 0.010966
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.28316 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | 0.13624 | 0.1973 | 0.05037 | 0.05037
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9481
[16 empty] | Humidity ratio (g/gda) | 0.015616 | 0.015616 | 0.015616 | 0.009184 | 0.009184 | 0.009184 | 0.009184 | 0.01094 | 0.011003 | 0.010974 | 0.010974
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | 0.13624 | 0.1973 | 0.05037 | 0.05037
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.66 | 12.7795 | 12.7795 | 12.7795 | 23.3321 | 24.4431 | 23.9365 | 23.9482
[16 empty] | Humidity ratio (g/gda) | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.004508 | 0.006264 | 0.006327 | 0.006298 | 0.006298
[16 empty] | Specific volume (L/kgda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Enthalpy (J/gda) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[16 empty] | Mass flow rate (kgda/s) | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.33354 | 0.13624 | 0.1973 | 0.13624 | 0.1973 | 0.05037 | 0.05037
* n/a = not applicable

## LCEM
Sec5-5out.XLS
Output spreadsheet for Airside Mechanical Equipment Diagnostic Tests: AE101-AE445
See "Adding Results" tab for more information. |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Paste new data in row 50 and below. |  |  |  | Life Cycle Energy Management Tool V3.10 | [5 empty] | Takasago Thermal Engineering, CO, JAPAN
Cells in blue are used in titles and labels |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | MLIT-TTE
Editing them here flows thru to other tabs |  |  |  | Program Name for Tables and Charts (short): |  |  |  | LCEM
To print pdf file, see instructions on "Read Me" tab. |  |  |  | Results Submission Date: |  |  |  | 2015-04-16 |  | Model / Organization Indentifier for Charts (short): |  |  |  | LCEM/MLIT-TTE | defaults to short program name / short organization name
Content Instructions
1. Use specified units
2. Data entry is restricted to the following ranges:
| C50..C52: | Software Name, Version, and Date of Results
| C61..J63: | Coil Loads, Fan Coil Air System, Cases AE101 - AE104
| S61..Y75: | Detailed Outputs, Fan Coil Air System, Cases AE101-AE104
| C89..J95: | Coil Loads, Single Zone Air System, Cases AE201 - AE245
| S89..Z123: | Detailed Outputs, Single Zone Air System, Cases AE201-AE245
| C137..O143: | Coil Loads, Constant Volume Terminal Reheat Air System, Cases AE301 - AE345
| S137..AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, Cases AE301-AE345
| C185..O191: | Coil Loads, Variable Air Volume Air System, Cases AE401 - AE445
| S185..AC219: | Detailed Outputs, Variable Air Volume Air System, Cases AE401-AE445
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | LCEM
| Version: | 3.10
| Date: | 2015-04-16
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | -2.931 | 0 | 0.5861 | 8.3722 | 0 | 0 | 0 | 6.8667 | [6 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.3977 | 29.0359 | 29.0359 | 29.6249 | 21.111 | 21.111
| AE103 | 0 | 1.465 | 0.5861 | 0 | 0.75229 | 0.010332 | 0.76262 | 32.5498 | [7 empty] | Humidity ratio (g/gda) | 0.00034449 | 0.0016965 | 0.0016965 | 0.0016965 | 0.0016965 | 0.0023731 | 0.0023731
| AE104 | 0 | 2.931 | 0.5861 | 0 | 3.3892 | 2.2564 | 5.6456 | 100 | [7 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | -28.3305 | 8.6805 | 33.542 | 33.542 | 34.1363 | 27.2632 | 27.2631
[17 empty] | Mass flow rate (kgda/s) | 0.11333 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 |  | Aug 7, 2015: Zone air mass flows set to "NA" by JN
[16 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.722 | 20.722 | 18.5081 | 19.0971 | 23.333 | 23.333 |  | Matches most recent output template.
[17 empty] | Humidity ratio (g/gda) | 0.0029339 | 0.004285 | 0.004285 | 0.004285 | 0.004285 | 0.0049605 | 0.0049605
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 23.0129 | 31.7233 | 31.7233 | 29.479 | 30.0761 | 36.0881 | 36.0881
[17 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
[16 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8932 | 24.8932 | 14.9194 | 15.5084 | 23.889 | 23.889
[17 empty] | Humidity ratio (g/gda) | 0.016761 | 0.013095 | 0.013095 | 0.010585 | 0.010585 | 0.011261 | 0.011261
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 69.7952 | 58.3823 | 58.3823 | 41.768 | 42.3718 | 52.6808 | 52.6808
[17 empty] | Mass flow rate (kgda/s) | 0.11333 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [9 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [8 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [8 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [8 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [6 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.931 | 0 | 0.5861 | 8.3021 | 0 | 0 | 0 | 6.8714 | [6 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.604 | 29.0359 | 29.0359 | 29.6249 | 21.111 | 21.111 | 21.406
| AE203 | 0 | 1.465 | 0.5861 | 0 | 0.81912 | 0.01125 | 0.83037 | 32.5498 | [7 empty] | Humidity ratio (g/gda) | 0.00034449 | 0.0016977 | 0.0016977 | 0.0016977 | 0.0016977 | 0.0023743 | 0.0023743 | 0.0023743
| AE204 | 0 | 2.931 | 0.5861 | 0 | 3.4558 | 2.2575 | 5.7133 | 100 | [7 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
| AE205 | 0 | 1.465 | 0.5861 | 0 | 1.8799 | 0.031088 | 1.911 | 44.2027 | [7 empty] | Enthalpy (J/gda) | -28.3305 | 8.8916 | 33.5449 | 33.5449 | 34.1393 | 27.2661 | 27.2661 | 27.5642
| AE206 | 0 | 1.465 | 0.5861 | 0 | 1.6456 | 1.0532 | 2.6988 | 100 | [7 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
| AE226 | 0 | 1.465 | 0.5861 | 0 | 1.5033 | 1.8877 | 3.3911 | 100 | [6 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9187 | 20.9187 | 18.5081 | 19.0971 | 23.333 | 23.333 | 23.628
| AE245 | 0 | 1.465 | 0.5861 | 0 | 2.1715 | 0.030615 | 2.2021 | 34.0684 | [7 empty] | Humidity ratio (g/gda) | 0.0029339 | 0.004285 | 0.004285 | 0.004285 | 0.004285 | 0.0049605 | 0.0049605 | 0.0049605
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 23.0129 | 31.9227 | 31.9227 | 29.479 | 30.0761 | 36.0881 | 36.0881 | 36.3875
[17 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[16 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.0893 | 25.0893 | 14.9194 | 15.5084 | 23.889 | 23.889 | 24.184
[17 empty] | Humidity ratio (g/gda) | 0.016761 | 0.013094 | 0.013094 | 0.010585 | 0.010585 | 0.011261 | 0.011261 | 0.011261
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 69.7952 | 58.5815 | 58.5815 | 41.768 | 42.3718 | 52.6808 | 52.6808 | 52.9836
[17 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[16 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.052 | 24.052 | 18.5198 | 19.1088 | 23.333 | 23.333 | 23.628
[17 empty] | Humidity ratio (g/gda) | 0.0044868 | 0.0058378 | 0.0058378 | 0.0058378 | 0.0058378 | 0.0065133 | 0.0065133 | 0.0065133
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 36.4725 | 39.05 | 39.05 | 33.4263 | 34.0251 | 40.0371 | 40.0371 | 40.3373
[17 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[16 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4187 | 23.4187 | 18.5759 | 19.1649 | 23.333 | 23.333 | 23.628
[17 empty] | Humidity ratio (g/gda) | 0.015546 | 0.014574 | 0.014574 | 0.013413 | 0.013413 | 0.014089 | 0.014089 | 0.014089
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 62.6628 | 60.6255 | 60.6255 | 52.6832 | 53.29 | 59.302 | 59.302 | 59.6063
[17 empty] | Mass flow rate (kgda/s) | 0.11327 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[16 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5759 | 19.1649 | 23.333 | 23.333 | 23.628
[17 empty] | Humidity ratio (g/gda) | 0.015546 | 0.015546 | 0.015546 | 0.013413 | 0.013413 | 0.014089 | 0.014089 | 0.014089
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 62.6628 | 62.6628 | 62.6628 | 52.6832 | 53.29 | 59.302 | 59.302 | 59.6063
[17 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
[16 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5096 | 19.0986 | 23.333 | 23.333 | 23.628
[17 empty] | Humidity ratio (g/gda) | 0.0044868 | 0.0044868 | 0.0044868 | 0.0044868 | 0.0044868 | 0.0051623 | 0.0051623 | 0.0051623
[17 empty] | Specific volume (L/kgda) | 833 | 833 | 833 | 833 | 833 | 833 | 833 | 833
[17 empty] | Enthalpy (J/gda) | 36.4725 | 36.4725 | 36.4725 | 29.992 | 30.5893 | 36.6013 | 36.6013 | 36.9008
[17 empty] | Mass flow rate (kgda/s) | 0.3398 | 0.3398 | 0.3398 | 0.3398 | 0.3398 | #N/A | 0.22654 | 0.22654
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 |  | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) |  | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | [14 empty] | AE301 | Dry bulb temperature (°C)
| AE303 | [15 empty] | Humidity ratio (g/gda)
| AE304 | [15 empty] | Specific volume (L/kgda)
| AE305 | [15 empty] | Enthalpy (J/gda)
| AE306 | [15 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
| AE326 | [14 empty] | AE303 | Dry bulb temperature (°C)
| AE345 | [15 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE304 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE305 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE306 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE326 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE345 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 |  | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) |  | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | [14 empty] | AE401 | Dry bulb temperature (°C)
| AE403 | [15 empty] | Humidity ratio (g/gda)
| AE404 | [15 empty] | Specific volume (L/kgda)
| AE405 | [15 empty] | Enthalpy (J/gda)
| AE406 | [15 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
| AE426 | [14 empty] | AE403 | Dry bulb temperature (°C)
| AE445 | [15 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE404 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE405 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE406 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE426 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
[16 empty] | AE445 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
[17 empty] | Mass flow rate (kgda/s) | [7 empty] | n/a* | n/a*
* n/a = not applicable

## TRNSYS
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | TRNSYS 17.01.0028 with TESS Libraries (and custom types) | [5 empty] | Thermal Energy System Specialists
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short): |  |  |  | TESS
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | TRNSYS
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2014-11-18 |  | Model / Organization Indentifier for Charts (short): |  |  |  | TRNSYS/TESS
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
| Software: | TRNSYS with TESS Libraries
| Version: | 17.01.0028
| Date: | 2014-11-18
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling | [5 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Ar | Air
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.931 | 0 | 0.5861 | 8.4159 | 0 | 0 | 0 | 6.3531 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.0054 | 29.309 | 29.309 | 29.9147 | 21.1138 | 21.1138
| AE103 | 0 | 1.465 | 0.5861 | 0 | 0.78002 | 0 | 0.78002 | 32.8657 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0022906 | 0.0022906
| AE104 | 0 | 2.931 | 0.5861 | 0 | 3.4932 | 2.0544 | 5.5475 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9366 | 787.163 | 859.0292 | 859.0292 | 856.5396 | 836.6855 | 836.6855
[16 empty] | Enthalpy (J/gda) | -28.5404 | 8.0312 | 33.5617 | 33.5617 | 34.1729 | 27.0593 | 27.0593
[16 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32964 | 0.32964 | 0.32964 | 0.32964 | #N/A | 0.21683
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7694 | 20.7694 | 18.5094 | 19.0931 | 23.3325 | 23.3325
[16 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0050086 | 0.0050086
[16 empty] | Specific volume (L/kgda) | 821.5721 | 838.436 | 838.436 | 831.9891 | 829.5769 | 846.6643 | 846.6643
[16 empty] | Enthalpy (J/gda) | 23.0203 | 31.8897 | 31.8897 | 29.598 | 30.1899 | 36.2163 | 36.2163
[16 empty] | Mass flow rate (kgda/s) | 0.11148 | 0.34036 | 0.34036 | 0.34036 | 0.34035 | #N/A | 0.22887
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8689 | 24.8689 | 14.9489 | 15.5247 | 23.8905 | 23.8905
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013062 | 0.013062 | 0.010612 | 0.010612 | 0.011291 | 0.011291
[16 empty] | Specific volume (L/kgda) | 872.9312 | 861.9835 | 861.9835 | 830.0764 | 827.6673 | 856.7579 | 856.7579
[16 empty] | Enthalpy (J/gda) | 69.8514 | 58.2895 | 58.2895 | 41.874 | 42.4646 | 52.7745 | 52.7745
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34114 | 0.34114 | 0.34114 | 0.34114 | #N/A | 0.23097
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.931 | 0 | 0.5861 | 8.3563 | 0 | 0 | 0 | 6.3531 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.1845 | 29.309 | 29.309 | 29.9147 | 21.1138 | 21.1138 | 21.3858
| AE203 | 0 | 1.465 | 0.5861 | 0 | 0.85249 | 0 | 0.85249 | 32.8591 | [6 empty] | Humidity ratio (g/gda) | 0.00025893 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0015953 | 0.0022906 | 0.0022906 | 0.0022906
| AE204 | 0 | 2.931 | 0.5861 | 0 | 3.5705 | 2.0544 | 5.6249 | 100 | [6 empty] | Specific volume (L/kgda) | 691.9366 | 787.6718 | 859.0292 | 859.0292 | 856.5396 | 836.6855 | 836.6855 | 835.563
| AE205 | 0 | 1.465 | 0.5861 | 0 | 1.9128 | 0 | 1.9128 | 44.5861 | [6 empty] | Enthalpy (J/gda) | -28.5404 | 8.2119 | 33.5617 | 33.5617 | 34.1729 | 27.0593 | 27.0593 | 27.3341
| AE206 | 0 | 1.465 | 0.5861 | 0 | 1.7033 | 0.96766 | 2.6709 | 100 | [6 empty] | Mass flow rate (kgda/s) | 0.11281 | 0.32964 | 0.32964 | 0.32964 | 0.32964 | #N/A | 0.21683 | 0.21683
| AE226 | 0 | 1.465 | 0.5861 | 0 | 1.5603 | 1.7951 | 3.3553 | 100 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9827 | 20.9827 | 18.5127 | 19.0964 | 23.3358 | 23.3358 | 23.6483
| AE245 | 0 | 1.465 | 0.5861 | 0 | 2.209 | 0 | 2.209 | 34.1009 | [6 empty] | Humidity ratio (g/gda) | 0.0029359 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0043297 | 0.0050086 | 0.0050086 | 0.0050086
[16 empty] | Specific volume (L/kgda) | 821.5721 | 839.0444 | 839.0444 | 831.9985 | 829.5862 | 846.6738 | 846.6738 | 845.3778
[16 empty] | Enthalpy (J/gda) | 23.0203 | 32.106 | 32.106 | 29.6013 | 30.1932 | 36.2197 | 36.2197 | 36.537
[16 empty] | Mass flow rate (kgda/s) | 0.11148 | 0.34036 | 0.34036 | 0.34036 | 0.34035 | #N/A | 0.22887 | 0.22887
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.089 | 25.089 | 14.949 | 15.5247 | 23.8905 | 23.8905 | 24.2165
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013062 | 0.013062 | 0.010612 | 0.010612 | 0.011291 | 0.011291 | 0.011291
[16 empty] | Specific volume (L/kgda) | 872.9312 | 862.62 | 862.62 | 830.0765 | 827.6674 | 856.758 | 856.758 | 855.3891
[16 empty] | Enthalpy (J/gda) | 69.8514 | 58.5163 | 58.5163 | 41.8741 | 42.4647 | 52.7746 | 52.7746 | 53.1094
[16 empty] | Mass flow rate (kgda/s) | 0.11017 | 0.34114 | 0.34114 | 0.34114 | 0.34114 | #N/A | 0.23097 | 0.23097
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0489 | 24.0489 | 18.5089 | 19.0924 | 23.3302 | 23.3302 | 23.6425
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0058881 | 0.0058881 | 0.0058881 | 0.0058881 | 0.0065687 | 0.0065687 | 0.0065687
[16 empty] | Specific volume (L/kgda) | 850.4379 | 849.9007 | 849.9007 | 834.0579 | 831.6391 | 848.7645 | 848.7645 | 847.465
[16 empty] | Enthalpy (J/gda) | 36.4891 | 39.1826 | 39.1826 | 33.5487 | 34.1421 | 40.1835 | 40.1835 | 40.5015
[16 empty] | Mass flow rate (kgda/s) | 0.11121 | 0.33952 | 0.33952 | 0.33952 | 0.33951 | #N/A | 0.2283 | 0.2283
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4334 | 23.4334 | 18.5234 | 19.1059 | 23.3365 | 23.3365 | 23.6483
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014551 | 0.014551 | 0.013376 | 0.013376 | 0.014065 | 0.014065 | 0.014065
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.8435 | 859.8435 | 844.0471 | 841.5963 | 858.9055 | 858.9055 | 857.5889
[16 empty] | Enthalpy (J/gda) | 62.7079 | 60.6005 | 60.6005 | 52.5481 | 53.1486 | 59.2623 | 59.2623 | 59.5841
[16 empty] | Mass flow rate (kgda/s) | 0.1099 | 0.3355 | 0.3355 | 0.3355 | 0.33549 | #N/A | 0.2256 | 0.2256
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.52 | 19.1025 | 23.3331 | 23.3331 | 23.6449
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.013373 | 0.013373 | 0.014062 | 0.014062 | 0.014062
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.942 | 859.942 | 844.0335 | 841.5827 | 858.8916 | 858.8916 | 857.5751
[16 empty] | Enthalpy (J/gda) | 62.7079 | 62.7079 | 62.7079 | 52.5373 | 53.1378 | 59.2514 | 59.2514 | 59.5732
[16 empty] | Mass flow rate (kgda/s) | 0.3355 | 0.3355 | 0.3355 | 0.3355 | 0.3355 | #N/A | 0.2256 | 0.2256
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5 | 19.0837 | 23.3227 | 23.3227 | 23.6352
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.00517 | 0.00517 | 0.00517
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4379 | 850.4379 | 832.1765 | 829.7636 | 846.8544 | 846.8544 | 845.558
[16 empty] | Enthalpy (J/gda) | 36.4891 | 36.4891 | 36.4891 | 29.9972 | 30.5893 | 36.617 | 36.617 | 36.9343
[16 empty] | Mass flow rate (kgda/s) | 0.34028 | 0.34028 | 0.34028 | 0.34028 | 0.34028 | #N/A | 0.22882 | 0.22882
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 2.9467 | 0 | 0 | 0 | 24.6351 | 7.7093 | 8.3843 | AE301 | Dry bulb temperature (°C) | -29 | 3.4295 | 7.22 | 7.22 | 7.7815 | 29.27 | 27.81 | 21.1102 | 22.2171 | 21.6678 | 22.0159
| AE303 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 6.7255 | 0 | 6.7255 | 48.1783 | 2.2552 | 2.4545 |  | Humidity ratio (g/gda) | 0.00025893 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0015419 | 0.0021868 | 0.0023719 | 0.00228 | 0.00228
| AE304 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 10.315 | 6.2615 | 16.5765 | 100 | 0.99153 | 1.5236 |  | Specific volume (L/kgda) | 691.9366 | 785.4602 | 796.2249 | 796.2249 | 793.9174 | 858.8449 | 854.6986 | 836.5361 | 839.9318 | 838.2465 | 836.8112
| AE305 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.3734 | 0 | 9.3734 | 65.7465 | 2.2567 | 2.4562 |  | Enthalpy (J/gda) | -28.5404 | 7.3163 | 11.1404 | 11.1404 | 11.7069 | 33.386 | 31.913 | 26.7919 | 28.3805 | 27.592 | 27.9436
| AE306 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.9149 | 5.4435 | 14.3584 | 100 | 2.2618 | 2.4621 |  | Mass flow rate (kgda/s) | 0.2814 | 0.77055 | 0.77055 | 0.77055 | 0.77055 | 0.35561 | 0.41494 | #N/A | #N/A | 0.48915 | 0.48915
| AE326 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.4705 | 12.3053 | 20.7757 | 100 | 2.2668 | 2.4678 | AE303 | Dry bulb temperature (°C) | 15.5 | 21.015 | 21.015 | 12.215 | 12.7861 | 19.18 | 18.75 | 23.3285 | 24.4389 | 23.8872 | 24.2266
| AE345 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.7073 | 0 | 9.7073 | 51.1113 | 2.2607 | 2.461 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0042356 | 0.0048998 | 0.0050898 | 0.0049954 | 0.0049954
[16 empty] | Specific volume (L/kgda) | 821.5721 | 839.0106 | 839.0106 | 813.9115 | 811.5517 | 833.7769 | 832.5505 | 846.506 | 849.9339 | 848.2307 | 846.8233
[16 empty] | Enthalpy (J/gda) | 23.0203 | 31.9 | 31.9 | 22.9778 | 23.5569 | 30.0395 | 29.6035 | 35.9355 | 37.5464 | 36.746 | 37.0906
[16 empty] | Mass flow rate (kgda/s) | 0.27808 | 0.7538 | 0.7538 | 0.7538 | 0.7538 | 0.34788 | 0.40592 | #N/A | #N/A | 0.47572 | 0.47572
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.5714 | 25.5714 | 12.2114 | 12.7819 | 15.59 | 16.48 | 23.8806 | 25.0027 | 24.4454 | 24.7871
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.012255 | 0.012255 | 0.0088543 | 0.0088543 | 0.0088543 | 0.0088543 | 0.0095252 | 0.0097162 | 0.0096213 | 0.0096213
[16 empty] | Specific volume (L/kgda) | 872.9312 | 862.9176 | 862.9176 | 819.9046 | 817.5256 | 829.612 | 832.1692 | 854.3402 | 857.8271 | 856.095 | 854.6649
[16 empty] | Enthalpy (J/gda) | 69.8514 | 56.9571 | 56.9571 | 34.6305 | 35.2138 | 38.085 | 38.995 | 48.2695 | 49.9048 | 49.0924 | 49.4423
[16 empty] | Mass flow rate (kgda/s) | 0.27553 | 0.74829 | 0.74829 | 0.74829 | 0.74829 | 0.34534 | 0.40296 | #N/A | #N/A | 0.47277 | 0.47277
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4732 | 24.4732 | 12.2132 | 12.7841 | 19.18 | 18.75 | 23.3269 | 24.4367 | 23.8854 | 24.2247
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0057938 | 0.0064597 | 0.0066501 | 0.0065555 | 0.0065555
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.9864 | 850.9864 | 815.9317 | 813.5654 | 835.8517 | 834.6222 | 848.608 | 852.0428 | 850.3362 | 848.9249
[16 empty] | Enthalpy (J/gda) | 36.4891 | 39.3742 | 39.3742 | 26.9085 | 27.489 | 33.9922 | 33.555 | 39.9028 | 41.5175 | 40.7152 | 41.0606
[16 empty] | Mass flow rate (kgda/s) | 0.27739 | 0.75194 | 0.75194 | 0.75194 | 0.75194 | 0.34702 | 0.40492 | #N/A | #N/A | 0.47454 | 0.47454
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7738 | 23.7738 | 12.2138 | 12.7843 | 19.19 | 18.76 | 23.3339 | 24.4427 | 23.8919 | 24.2309
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.01181 | 0.01181 | 0.0088557 | 0.0088557 | 0.0088557 | 0.0088557 | 0.0095248 | 0.0097161 | 0.0096211 | 0.0096211
[16 empty] | Specific volume (L/kgda) | 859.942 | 857.1235 | 857.1235 | 819.9131 | 817.5341 | 839.9574 | 838.7219 | 852.7674 | 856.2158 | 854.5024 | 853.0834
[16 empty] | Enthalpy (J/gda) | 62.7079 | 53.9762 | 53.9762 | 34.6363 | 35.2197 | 41.7693 | 41.3297 | 47.7088 | 49.3311 | 48.525 | 48.8722
[16 empty] | Mass flow rate (kgda/s) | 0.27604 | 0.74829 | 0.74829 | 0.74829 | 0.74829 | 0.34533 | 0.40295 | #N/A | #N/A | 0.47224 | 0.47224
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2 | 12.7705 | 19.19 | 18.76 | 23.3337 | 24.4424 | 23.8916 | 24.2307
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.0088476 | 0.0088476 | 0.0088476 | 0.0088476 | 0.0095166 | 0.009708 | 0.0096129 | 0.0096129
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.942 | 859.942 | 819.863 | 817.4842 | 839.9466 | 838.7111 | 852.7558 | 856.2039 | 854.4907 | 853.0715
[16 empty] | Enthalpy (J/gda) | 62.7079 | 62.7079 | 62.7079 | 34.6018 | 35.185 | 41.7487 | 41.3091 | 47.6878 | 49.31 | 48.504 | 48.8512
[16 empty] | Mass flow rate (kgda/s) | 0.74833 | 0.74833 | 0.74833 | 0.74833 | 0.74833 | 0.34536 | 0.40298 | #N/A | #N/A | 0.47229 | 0.47229
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.2 | 12.7711 | 19.18 | 18.75 | 23.328 | 24.4382 | 23.8867 | 24.2261
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0051553 | 0.0053453 | 0.0052509 | 0.0052509
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4379 | 850.4379 | 814.2005 | 811.8397 | 834.1168 | 832.8898 | 846.8497 | 850.2785 | 848.5748 | 847.1665
[16 empty] | Enthalpy (J/gda) | 36.4891 | 36.4891 | 36.4891 | 23.6068 | 24.186 | 30.687 | 30.2508 | 36.5851 | 38.1965 | 37.3958 | 37.7406
[16 empty] | Mass flow rate (kgda/s) | 0.75354 | 0.75354 | 0.75354 | 0.75354 | 0.75354 | 0.34776 | 0.40578 | #N/A | #N/A | 0.47557 | 0.47557
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 10.2578 | 0 | 0 | 0 | 4.1464 | 4.4895 | 4.8689 | AE401 | Dry bulb temperature (°C) | -29 | -28.9976 | 7.22 | 7.22 | 7.2949 | 46.8281 | 35.9884 | 21.1151 | 22.2211 | 21.1151 | 21.1151
| AE403 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 1.4476 | 0 | 1.4476 | 36.3722 | 0 | 0 |  | Humidity ratio (g/gda) | 0.00025893 | 0.00025899 | 0.00025893 | 0.00025893 | 0.00025893 | 0.00026343 | 0.00025893 | 0.0022691 | 0.0022892 | 0.0022691 | 0.0022691
| AE404 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 7.3862 | 5.9214 | 13.3076 | 100 | 0 | 0 |  | Specific volume (L/kgda) | 691.9366 | 691.9435 | 794.5864 | 794.5864 | 794.2783 | 906.845 | 876.1179 | 836.6603 | 839.8318 | 836.6603 | 836.6603
| AE405 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.091 | 0 | 4.091 | 53.4325 | 0 | 0 |  | Enthalpy (J/gda) | -28.5404 | -28.5378 | 7.9144 | 7.9144 | 7.9897 | 47.7909 | 36.8692 | 27.006 | 28.1742 | 27.006 | 27.006
| AE406 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.6296 | 4.5892 | 8.2187 | 100 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.2814 | 0.2814 | 0.2814 | 0.2814 | 0.2814 | 0.11282 | 0.16858 | #N/A | #N/A | 0 | 0
| AE426 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 3.5849 | 5.2196 | 8.8045 | 100 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.9405 | 16.9405 | 12.6692 | 12.7822 | 12.7822 | 12.7822 | 23.3302 | 24.4386 | 23.9452 | 23.95
| AE445 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 4.1448 | 0 | 4.1448 | 49.5567 | 0 | 0 |  | Humidity ratio (g/gda) | 0.0029359 | 0.0032912 | 0.0032912 | 0.0032904 | 0.0032889 | 0.0032889 | 0.0032889 | 0.0049882 | 0.0050489 | 0.0050219 | 0.0050219
[16 empty] | Specific volume (L/kgda) | 821.5721 | 826.1416 | 826.1416 | 813.9765 | 813.5066 | 814.2962 | 814.2962 | 846.6302 | 849.8778 | 848.4319 | 848.4118
[16 empty] | Enthalpy (J/gda) | 23.0203 | 25.3772 | 25.3772 | 21.0521 | 21.1625 | 21.1625 | 21.1625 | 36.1621 | 37.442 | 36.8722 | 36.8771
[16 empty] | Mass flow rate (kgda/s) | 0.27808 | 0.33495 | 0.33495 | 0.33495 | 0.33495 | 0.13681 | 0.19814 | #N/A | #N/A | 0.056872 | 0.056872
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.721 | 25.721 | 12.491 | 12.7811 | 12.7878 | 12.7878 | 23.8829 | 24.9989 | 24.3678 | 24.474
[16 empty] | Humidity ratio (g/gda) | 0.016774 | 0.013494 | 0.013494 | 0.009021 | 0.009017 | 0.009021 | 0.009021 | 0.0099213 | 0.010261 | 0.010067 | 0.010067
[16 empty] | Specific volume (L/kgda) | 872.9312 | 865.0361 | 865.0361 | 820.9246 | 819.6593 | 821.7776 | 821.7776 | 854.883 | 858.5556 | 856.4754 | 856.0296
[16 empty] | Enthalpy (J/gda) | 69.8514 | 60.2687 | 60.2687 | 35.3369 | 35.6235 | 35.6405 | 35.6405 | 49.2802 | 51.2876 | 50.1471 | 50.256
[16 empty] | Mass flow rate (kgda/s) | 0.27532 | 0.53883 | 0.53883 | 0.53883 | 0.53882 | 0.25786 | 0.28097 | #N/A | #N/A | 0.2635 | 0.2635
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7397 | 24.7397 | 12.6697 | 12.7825 | 12.7825 | 12.7825 | 23.3319 | 24.4401 | 23.9467 | 23.9515
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.004835 | 0.004835 | 0.004835 | 0.004835 | 0.004835 | 0.004835 | 0.0065372 | 0.006598 | 0.0065709 | 0.0065709
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4473 | 850.4473 | 815.9886 | 815.5201 | 816.3107 | 816.3107 | 848.7271 | 851.9817 | 850.5325 | 850.5124
[16 empty] | Enthalpy (J/gda) | 36.4891 | 37.2029 | 37.2029 | 24.9519 | 25.0664 | 25.0664 | 25.0664 | 40.1052 | 41.3882 | 40.8169 | 40.8218
[16 empty] | Mass flow rate (kgda/s) | 0.27739 | 0.33393 | 0.33393 | 0.33393 | 0.33393 | 0.13639 | 0.19754 | #N/A | #N/A | 0.056539 | 0.056539
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1572 | 23.1606 | 12.6584 | 12.7709 | 12.7709 | 12.7709 | 23.318 | 24.431 | 23.9345 | 23.9393
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.014766 | 0.014801 | 0.0091221 | 0.0091221 | 0.0091221 | 0.0091221 | 0.010838 | 0.0109 | 0.010873 | 0.010873
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.3332 | 859.3905 | 821.5375 | 821.0663 | 821.8609 | 821.8609 | 854.4955 | 857.7874 | 856.3189 | 856.2989
[16 empty] | Enthalpy (J/gda) | 62.7079 | 60.8624 | 60.9557 | 35.7636 | 35.8787 | 35.8787 | 35.8787 | 51.0348 | 52.3348 | 51.7549 | 51.7598
[16 empty] | Mass flow rate (kgda/s) | 0.27552 | 0.33137 | 0.33137 | 0.33137 | 0.33137 | 0.13538 | 0.19599 | #N/A | #N/A | 0.055858 | 0.055858
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.67 | 12.7822 | 12.7822 | 12.7822 | 23.3286 | 24.4416 | 23.9452 | 23.9499
[16 empty] | Humidity ratio (g/gda) | 0.015556 | 0.015556 | 0.015556 | 0.0091292 | 0.0091292 | 0.0091292 | 0.0091292 | 0.010844 | 0.010906 | 0.010879 | 0.010879
[16 empty] | Specific volume (L/kgda) | 859.942 | 859.942 | 859.942 | 821.58 | 821.1102 | 821.9025 | 821.9025 | 854.534 | 857.8259 | 856.3576 | 856.3375
[16 empty] | Enthalpy (J/gda) | 62.7079 | 62.7079 | 62.7079 | 35.7933 | 35.908 | 35.908 | 35.908 | 51.0608 | 52.3607 | 51.7809 | 51.7858
[16 empty] | Mass flow rate (kgda/s) | 0.33133 | 0.33133 | 0.33133 | 0.33133 | 0.33133 | 0.13536 | 0.19597 | #N/A | #N/A | 0.055831 | 0.055831
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.67 | 12.7825 | 12.7825 | 12.7825 | 23.3321 | 24.442 | 23.9476 | 23.9524
[16 empty] | Humidity ratio (g/gda) | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0044909 | 0.0061921 | 0.006253 | 0.0062259 | 0.0062259
[16 empty] | Specific volume (L/kgda) | 850.4379 | 850.4379 | 850.4379 | 815.5415 | 815.0746 | 815.8626 | 815.8626 | 848.2614 | 851.5195 | 850.0683 | 850.0482
[16 empty] | Enthalpy (J/gda) | 36.4891 | 36.4891 | 36.4891 | 24.0835 | 24.1977 | 24.1977 | 24.1977 | 39.2271 | 40.5117 | 39.9395 | 39.9444
[16 empty] | Mass flow rate (kgda/s) | 0.33411 | 0.33411 | 0.33411 | 0.33411 | 0.33411 | 0.13647 | 0.19764 | #N/A | #N/A | 0.056569 | 0.056569
* n/a = not applicable

## blank
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Blank
1. Use specified units. |  |  |  | Program Version Release Date: | [5 empty] | Modeler Organization for Tables and Charts (short):
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | Blank
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: | [5 empty] | Model / Organization Indentifier for Charts (short): | Blank
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
Software:
Version:
Date:
Last Hour of Simulation - Summary Outputs - Fan Coil Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling |  |  | Last Hour of Simulation - Detailed Outputs - Fan Coil Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet |  |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH |  |  |  |  | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) |  |  |  |  | Air | Air | Outlet | Outlet | Air | Ar
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) |  |  | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1)
| AE101 | 2.93 | [9 empty] | AE101 | Dry bulb temperature (°C)
| AE103 | [11 empty] | Humidity ratio (g/gda)
| AE104 | [11 empty] | Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE103 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE104 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
Last Hour of Simulation - Summary Outputs - Single Zone Air Handler
|  | Zone | Zone | Zone | Heating | Cooling Coil |  |  | Cooling |  |  | Last Hour of Simulation - Detailed Outputs - Single Zone Air Handler
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet |  |  |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH |  |  |  |  | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) |  |  |  |  | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%) |  |  | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.93 | [9 empty] | AE201 | Dry bulb temperature (°C)
| AE203 | [11 empty] | Humidity ratio (g/gda)
| AE204 | [11 empty] | Specific volume (L/kgda)
| AE205 | [11 empty] | Enthalpy (J/gda)
| AE206 | [11 empty] | Mass flow rate (kgda/s)
| AE226 | [10 empty] | AE203 | Dry bulb temperature (°C)
| AE245 | [11 empty] | Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE204 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE205 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE206 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE226 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)
[12 empty] | AE245 | Dry bulb temperature (°C)
Humidity ratio (g/gda)
Specific volume (L/kgda)
Enthalpy (J/gda)
Mass flow rate (kgda/s)